## BOQ
The International Committee of the Red Cross
WATER & HABITAT DEPARTMENT
Zaidan PHCC / RO / Install
Zaidan / Abu Ghraib / Baghdad Governorate
Feb 2017
Zaidan PHCC / RO / Install
Zaidan / Abu Ghraib / Baghdad Governorate
Item | Description | Unit | Qty | Unit Price (USD) | Total Price (USD)
1 | Intake
1.1 | Submersible pump: Supply, install, connect and test new raw water submersible pump (of best quality-western origin), Pump capacity (Q = 5 m3/h, H = 40 m, 220-240 V single PH). The work includes all needed valves, unions, non return valves & electrical wirings for connection to the nearest power source, proper switch and protection. the pump should be installed in the adjacent concrete lined canal of Abu Ghraib, the work includes proper installation and fixation of the pump to ensure functional operation without vibrations or displacement of the pump and all that's required to operate the pump functionally and successfully | ea. | 1 | 0 | 0
1.2 | Piping: Provision of materials and work to supply, install, connect and test galvanized water pipes (1'') for raw water delivery from the submersible pump to the RO unit initial Storage tank.The work includes all the necessary fittings, valves wherever needed and the required supports, the pipe should be buried in the soil at a minmum 0.5 m depth, buried pipe should be wrapped with insulation tape for protection. | ml | 370 | 0 | 0
| Total |  |  |  | 0
2 | Civil Works
2.1 | Backfilling: Provision of materials and work to back fill with Sub base layer of (10 cm) for dimensions (6m X 6m) using mechanical compactor.work includes the required watering and compacting till reaching the required height and achieve very hard stratum. | m3 | 3.6 | 0 | 0
2.2 | Concrete base: Provision of material and work to cast reinforced concrete base (5 m X 5 m X 0.3 m). Concrete mix 1:2:4 of 30 cm thick, using SR cement, and the required expansion joints (2) cm every (2)m length filled with mastic of best quality (Jordanian origin); The reinforcement is two layers of BRC (D6, WWM 15 X 15cm). The reinforcement mesh (B.R.C) have to be brand new, clean, and free from any dirt or rust,, (All work has to be done as per the technical specifications). | m3 | 7.5 | 0 | 0
2.3 | Sunshade: Provision of materials and work to manufacture and erect new protection sunshade with external dimensions of (6m X6m, 3.5m height), to protect the RO unit. Sunshade should be made using galvanized steel columns of 3" dia. and corrugated galvanized steel sheets of gauge 22 to be fixed by means of hooks with the steel structure of angle section beam of (2.5" X 2.5" X 3/8") and hollow pipe of (2" X 4"). Work includes painting the steel structure with one layer of anticorrosion paint then three layers of oil paint of good quality. | m2 | 36 | 0 | 0
2.4 | Fence: Provision of materials and work to manufacture and erect new BRC fence of 1.8m height, to protect the RO unit, using galvanized BRC (70mm mesh) . Work includes, supply and install BRC gate of dimensions (1.8m X 2m), required reinforced concrete posts or similar for supports and gate fixation. | ml | 24 | 0 | 0
| Total |  |  |  | 0
3 | RO Unit works
3.1 | RO unit: Provision of material and work to supply and install completed Reverse Osmosis unit of capacity 3 m3/h, all components should be of European or equivalent western origin to be assembled in Iraq on a proper stainless steel structure. The work should include: - Sand filter with backwash option to remove sediment and turbidity. - Activated Carbon filters to remove unpleasant tastes, odours, dechlorination, and organic contaminant adsorption. - Cartridge filters to remove micro organic materials, heavy materials & to protect the RO membranes -Water Softener System - Reverse Osmosis - 5 MEMBRANES of US origin, with the required pump sets (Italian or equivalent western origin) to purify water and remove salts and others impurities, also capable of rejecting Bacteria, particles, dyes, and other constituents - Hypochlorite disinfection unit (2 mixing tanks and dosing pumps) for disinfection against all the microbiological contaminants Also work include, the electrical control panel (schneider or equivalent western origin) , all the electrical connection, cables, piping connections , fittings and required accessories for the installation and functioning successfully. The contractor should provide: 1- on-site training to the responsible authority staff on how to operate and maintain the unit. 2- the required consumables for operating period of 3 months. | ea. | 1 | 0 | 0
3.2 | Polypropylene water pipes: Provision of material and work to supply, install, connect and test Polypropylene water pipes for treated water of 20mm diameter, the work includes all the necessary fittings, valves wherever needed and the required supports . | ml | 15 | 0 | 0
3.3 | Ditto, but PVC (2") dia. For drainage effluent | ml | 25 | 0 | 0
3.4 | PVC storage tank: Supply, install, connect and test PVC storage tank of capacity (10 m3) of best quality, 1 tank for raw water and 1 for treated water, the work includes all the required piping and valves connection and fixation for best operation . | ea. | 2 | 0 | 0
3.5 | Treated Water Pump: Provision of materials and work to supply, install and operate a new water pump, 3/4 '' of western origin (H=20 m, Q=50 liter/min) to pump the water from the treated water tank to the existing roof storage tanks of the PHCC.The work includes all needed piping, gate valve, unions, non return valves & electrical wirings, selector switch to switching between in use and stand by pump and the fixation, test to ensure no leakages. | ea. | 2 | 0 | 0
3.6 | Treated water Piping: Provision of materials and work to supply, install, connect and test galvanized water pipes (0.5'') for the treated water from the storage tank to the existing roof tanks of the PHCC. The work includes all the necessary fittings, valves wherever needed and the required supports and fixation to ensure the best quality of installation. | m.l | 40 | 0 | 0
| Total |  |  |  | 0
4 | Electrical works.
4.1 | Cables: Supply, install and connect power cable of size (4 X16 mm2) for the RO unit, the work includes all the accessories of terminals, fixation, and connection for best connection and operation. | m.l | 15 | 0 | 0
4.2 | Electrical Float switch :Provision of materials and work to supply, install and operate electrical float (to control the operation of RO unit with the necessary interlock of the two floats) with all needed wiring and requirements to finish the work, to be connected at the raw water tank. | ea. | 1 | 0 | 0
4.3 | Circuit Breaker of 75 Amps: Supply, install, connect and test new MCCB of 75 Amps adjustable for the RO unit, to be connected on the main cable of the RO unit, western origin, to be fixed inside suitable box. Work includes all connections and accessories needed to complete the job. | ea. | 1 | 0 | 0
4.4 | External lighting:Provision of material and work to make the job complete in every part and details to Supply and install weatherproof outdoor type (500 W) light projector complete with frame, support, necessary wiring (2 X 2.5 mm2) and switch. The projector should be fixed on the new sun shade structure firmly. | ea. | 2 | 0 | 0
| Total |  |  |  | 0
| Grand Total |  |  |  | 0
| Estimated duration | n° of calendar days