## BoQ
The International Committee of the Red Cross
WATER & HABITAT DEPARTMENT
Anbar / Emergency / IDPs Response (2017) Qanater / CU / Rehabilitation
Garma Markaz / Garma / Anbar Governorate
2017-03-23
Anbar / Emergency / IDPs Response (2017)
Qanater / CU / Rehabilitation
Garma Markaz / Garma / Anbar Governorate
Item | Description | Unit | Qty | Unit Price (USD) | Total Price (USD)
1 | Low lift station
1.1 | Supply, install and connect brand new submersible pump of Turkish origin ( standart or similar brand) and capacity (Q = 200 m3/hr, H = 20 m, 3 ph, 380 V, 50 Hz). The work includes dismantling the damaged submersible pump and submitting them to the plant administration, proper cable feeder to connect the submersible pumps systematically with the existing cables using proper cable joints with all requirements to achieve a complete electrical connection, testing and successfully operation. | ea. | 2
1.2 | Supply, install, connect and operate new electrical starter of 22kW for the new submersible pump. The work includes all required equipment, materials and labors for interlock connection, protection, indicators, and fixing, in addition to all requirements and accessories to complete the work successfully. | ea. | 2
1.3 | Provision of materials and work to supply, extend and connect new galvanized steel pipe of (6") to connect the submersable pump with the non return valve, the work includes the required fittings and the required accessories (flanges, elbows, reducer, etc.). | m.l | 6
1.4 | Supply, install and operate new non return valves, double flanged swing type, (6" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea. | 2
1.5 | Supply, install and operate new Butterfly valves (Turkish origin), double flanged, (6") with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea. | 2
1.6 | Provision of materials and work to supply, install and connect power cable of size (4 X 16 mm2) for the new submersible pump, the work includes all the accessories of terminals, fixation, and connection | ml | 50
Total
2 | Settling tank
2.1 | Provision of material and work to repair and operate the affected parts of whole settling tank and the associated tanks (of dimensions 12m x 2.4m x 2.4m) after properly emptying them. The work includes completely washing and cleaning the walls and bottom using electric steel brush to clean rust area , removing all the accumulative sludge and heavy stacks of mud, cleaning and unclogging the sludge discharge pipes, repairing any defected parts in internal and external walls, bottom, V-notch and repairing any leakage points, replace the damage and missing steel plates in order to restore the tank as per its original design, including replacing the damaged bracing iron angle, painting with (2) layers of drinking water epoxy paint for the internal walls and externally with suitable oil paint after prime painting of anti-rust with all requirements to complete the job perfectly. | ea. | 2
2.2 | Provision of material and work to maintain and repair the intermediate tank of dimenssions ( 6m x 2.4m x 2.4m ), The work includes completely washing and cleaning the walls and bottom, removing all the accumulative sludge , cleaning and unclogging the sludge discharge pipes, replace the damage and missing plates in order to restore the tank as per its original design,painting the interior surface with two layers of drinking water epoxy paint and the externally with suitable oil paint after prime painting of anti-rust with all requirements to complete the job perfectly, also work includes repairing the leakages. | ea. | 1
2.3 | Provision of materials and work to supply and install flocculator complete with steel shaft and propeller (motor of 1.1kw). The work includes all the required material and tools to install,cable connection, electrical starter, test and successfully operate the new one. | ea. | 2
2.4 | Provision of materials and work to supply and install flash mixer complete with steel shaft and propeller (motor of 1.2 kw). The work includes all the required material and tools to install, cable connection, electrical starter, test and successfully operate the new one. | ea. | 2
2.5 | Provision of materials and work to supply and install clean out and drain valves (3"). The work includes required piping and flanges, testing and operating. | ea. | 8
2.6 | Provision of materials and work to supply and install valves (8"). The work includes dismantling the existing damaged ones, testing and operating. | ea. | 2
Total
3 | High lift station
3.1 | Provision of material and work to make the job complete in every part and details to supply, install and connect new HLP horizontal (complete with motor) of Q = 200 m3/h, H = 60m, 1500 r.p.m, 3 ph, V=380, type ( Almas or similar brand), Turkish origin. The work includes, dismantle the existing damaged pump, the modification of the suction and delivery pipes with all the accessories (anchor bolt, rubber washers, flanges, pressure gauges, connection cables, necessary pump alignment and fixation, testing and commissioning). The new HLP shall be connected to the existing control panel and starter with a proper length of cable , with all the requirements to achieve a proper and neat performance according to the instructions of the ICRC Engineer. Testing and successfully operating are included in the price. | ea. | 2
3.2 | Supply, install, connect and operate new electrical starter of 55kW for the high lift pump. The work includes all required equipment, materials and labors for interlock connection, protection, indicators, and fixing, in addition to all requirements and accessories to complete the work successfully. | ea. | 2
3.3 | Supply, install and operate new Butterfly valves (Turkish origin), double flanged, (6" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea. | 4
3.4 | Supply, install and operate new non return valves, double flanged swing type, (6" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea. | 2
3.5 | Supply, install and operate new Flexible Joint, double flanged, (6") with all accessories , the works including all the rubber washers and all piping modification. | ea. | 2
3.6 | Provision of materials and work to supply, install and connect power cable of (4 X 35mm) size , the work includes all the accessories of terminals, fixation, and connection. | ml | 30
Total
4 | Pressure filters
4.1 | Provision of material and work to maintian, repair and operate the pressure filters, the work includes, repair the leakages, required welding of the nozzle base plate and fixed support, maintain and cleaning the filter (internally), coating the internal side with two layers of drinking water epoxy and externally with suitable oil paint after the red oxide prim, supply and install nozzles , replace the defected or improper parts with new ones such as (washers, manometer gauge, bolts.). | ea. | 2
4.2 | Provision of materials and work to make the job complete in every part and detail, to supply filter media and change the existing damaged media according to (GDoW) specification , (The contractor should provide test certificate from supplier showing the grade and sieve numbers of media). The price shall include all required materials, labor, and accessories to implement the work properly and functionally. | m3 | 30
4.3 | Provision of materials and work to supply and install pressure relief valve . The work includes testing and operating. | ea. | 2
4.4 | Provision of materials and work to supply and install valve (4"). The work includes all required material and tools, testing and operating. | ea. | 10
4.5 | Provision of materials and work to supply and install Air Blower of capacity (11 - 14 kW). The work includes required fittings and accessories,to make the job completed in every part and details | ea. | 2
Total
5 | Chlorination system.
5.1 | Dosing pump :Provision of materials and work to supply and install brand new Hypochlorite dosing pump, western origin of capacity (Q=8-20 l/hr, & H= 6 bar) . The work includes installion and fixing work. Price includes; the required electrical connections, cable and MCB. Testing and operating the pump to insure proper performance. . | ea. | 1
5.2 | Hypochlorite mixer :Provision of materials and work to Supply and install brand new Hypochlorite mixer of a specification (0.37-0.7 kW, 1000 rpm, 0.9 m length stainless steel shaft, and propeller). The work includes; supply and install new water polyethylene tank of 1m3 capacity, electrical connections, cable, MCB and needed accessories for installation, . Testing and successfully operating. | ea. | 1
5.3 | Piping System: Supply and install new PVC & GS pipes, valves and accessories of different sizes proper for the hypochlorite unit completely. The work includes extending new pipe, fixation and supports with all required piping to complete work , testing and successfully operating. | ea. | 1
5.4 | Provision of material and work to supply and install brand new Chlorinators of western origin (dosing equipment) wall mounted, of a capacity of (1Kg/h), ALLDOS type. The work includes the necessary fixation of the injector and the dosing device, supply, install and connect PVC pipe of 1" of a required length, all necessary fittings and strainer, non return valve. the work also includes the connection with the injection point on the discharge pipe in addition to the injection points of pre-chlorination in the settling tank with all required PVC piping and valves to control the dosing amount through both the pre-chlorination point and the delivery pipe, required frame and base, Testing and operating the chlorinators functionally and successfully. | ea. | 1
5.5 | Provision of material and work to supply, install and operate Chlorinator Boosting Pump (Q=2m3/h, H=80m) western origin, the work include the electrical starter (1.5KW), electrical connection, supply and connect galvanized pipe of 1" with all the necessary fittings | ea. | 1
Total
6 | Alum system.
6.1 | Provision of material and work to supply and install brand new Alum system completed (dosing pump no.1, Alum mixture no.1, Alum tank no.1), The work includes supply and install all the required galvanized and PVC piping with all fittings and accessories , flexible hose, wiring, cables. | ea. | 1
Total
7 | Main control panel, cables and site works
7.1 | Provision of materials and work to make the job complete in every parts and details to maintian and repair the (main control panel), The work include supply and install , main MCCB of (400 A) No.1, replace the damaged protection and control device , phase failure and over under voltage protection device (Volts =380 V, Hz=50, adjustable voltage range 335-405 V), The works includes all the necessary wiring, indication lamps, Ammeters, voltmeter with selector switch, terminals, cable glands and fixation, All the electrical provided materials, should be brand new and of western origin. | ea. | 1
7.2 | Provision of material and work to Supply, install, connect and test new manual transfering switch of 600 Amps, to be fixed inside suitable box. Work includes all connections and accessories needed to complete the job. | ea. | 1
7.3 | Provision of materials and work to supply, install and connect power cable of (4 X 95 mm) size , the work includes all the accessories of terminals, fixation, and connection. | ml | 60
7.4 | Provision of materials and work to supply, install and connect control cable of (8 X 1.5 mm) size , the work includes all the accessories of terminals, fixation, and connection. | ml | 450
7.5 | Provision of materials and work to supply, install and connect power cable of (4 X 2.5mm) size , the work includes all the accessories of terminals, fixation, and connection. | ml | 60
7.6 | Provision of material and work to make the job complete in every part and details to Supply and install weatherproof outdoor type (250 W) mercury bulb light projector complete with frame, support, necessary wiring (2 X 2.5 mm2) and switch. | ea. | 6
7.7 | Provision of material and work to make the job complete in every part and details to repair the existing damaged shade, the work includes supply install and fix new corrugated sheet to replace the affected sheets of the existing shed, replace the damaged steel sections, the required fixation, oil paint, and required accessories | m2 | 55
Total
Grand Total
| Duration | n° of calendar days