## BoQ
The International Committee of the Red Cross
WATER & HABITAT DEPARTMENT
Mosul response (2017) Shirqat Unified / WTP 4,000m3/h / Installation
Markiz Shirqat / Shirqat / Salah al Din Gov
Bidder's Quotations
Mosul response (2017) Shirqat Unified / WTP 4,000m3/h / Installation
Markiz Shirqat / Shirqat / Salah al Din Gov
Item | Description | Unit | Qty | Unit Price (USD) | Total Price (USD)
1 | Intake :
1.1 | Provision of materials, tools, and labors to restore the improper and in-completed back washing system at intake. Work includes; the required pipe connections & fittings of (150) mm and others sizes fit for the system requirements to ensure effective cleaning process for the existing foot valve size (800) mm with all requirements (fixture, welding, painting, etc.) to complete the job neatly. Test & operate successfully | ls. | 1
total
2 | Low Lift Station:
2.1 | Provision of materials, tools, and labor to supply, Install & operate new low lift horizontal pump-set, split-case, IDEAL brand, stainless steel shaft & impeller (as per manufacturer grade) of specification (Q = 1400 m3/h, H = 15 m, 92 kW - VEMAT motor) for line - no1. Work includes; dismantling of the old pump-set, making the required modification for the inlet / oulet along with the steel and concrete base to fit the installation of the new set into position neatly. Price include; new soft starter and MCCBs (ABB type) fit to the motor capacity, with all relevant electro-mechanical connections as standard to achieve neat performance. | ea. | 1
2.2 | Provision of materials, tools, and labor to overhaul the existing split-case pump (Q = 1400 m3/h, H = 15 m) line - no 2 / 3. The work includes; the disassembling & assembling, replacing the defective and exhausted parts such as (ball bearings, glands, packing, mechanical seals, coupling, greasing, wear rings, etc.). Price also; checking and maintaining the steel Shaft, & impeller (replace if required) with all requirements and standard electro-mechanical connections to achieve neat performance. Testing and operating successfully. | ea. | 2
2.3 | Provision of materials, tools, and labor to supply and install new high quality mechanical flanged check valve with lever, Turkish origin (FaF or Duyar brand) of size (500 mm) to replace the old valve on delivery pipe, making the required modification to fit the installation of the new valve into position neatly. Testing for no leakage. | ea. | 5
2.4 | Provision of materials, tools, and labor to repair butterfly - double flange valve with gearbox of (500) mm on incoming pipe. Work includes; maintaining / or replacing any defective part (disc, spindle, sealant, etc.) to ensure effective operating. Testing and Check for no leakage | ea. | 4
total
3 | High Lift Station :
3.1 | Supply and Install new High lift horizontal pump-set, split-case, IDEAL brand, Spanish origin, stainless steel shaft (as per manufacturer grade) & Bronze impeller, of specification (Q = 750 m3/h, H = 85 m, 250 kW - VEMAT motor) for the Center sets - line no1. Work includes; dismantling the old pump-set, making the required modification for the inlet / outlet, steel / concrete base to fit the installation of the new pump-set into its position neatly. Price include; new soft starter and MCCBs (ABB type) fit to motor capacity, with all related electro-mechanical connections and requirements and as standard to achieve perfect performance. | ea. | 1
3.2 | Ditto; but for the HLP set of specifications (Q=500 m3/ h, H = 95 m, 200 kW - VEMAT motor) for the Northern set - line no 1. | ea. | 1
3.3 | Ditto; but for the HLP set of specifications (Q=750 m3/ h, H = 125 m, 400 kW - VEMAT motor) for the Southern set - line no 1. | ea. | 1
3.4 | Provision of materials, tools, and labor to overhaul the existing split-case pump of specification (Q = 750 m3/h, H = 125 m) for the Southern set - line no 3. The work includes; the disassembling, replacing the defective and exhausted parts (ball bearings, glands, packing, mechanical seals coupling, shaft, impeller, etc.). Price also; check the elect. control panel components (replace the defected parts - if required) with all requirements and standard electro-mechanical connections to achieve perfect performance. Testing and operating successfully | ea. | 1
3.5 | Ditto; but for split-case pump of specification (Q = 500 m3/h, H = 95 m) for the Northern set - line no 3. | ea. | 1
3.6 | Ditto; but for split-case pump of specification (Q = 750 m3/h, H = 85 m) for the Center set - line no 3. | ea. | 1
3.7 | Provision of materials, tools, and labor to supply and install new high quality mechanical flanged check valve with lever, Turkish origin (FaF or Duyar brand) of size (400) mm to replace the defective one on the delivery pipe. Testing for no leakage. | ea. | 9
3.8 | Provision of materials, tools, and labor to supply and install new high quality electric actuator (AUMA Riester GmbH & Co KG brand, German origin) or equivalent (type to be approved by ICRC) to replace the defective / improper one fixed on the butterfly valve size (400) mm on the delivery pipe. The motor drive capacity must be fit for the existing valve requirements. Testing and operating successfully. | ea. | 7
3.9 | Provision of materials, tools, and labor to repair and operate the existing electric actuator mounted on the valve (400) mm. The work includes; the dismantling and installation, replacing any defective / improper electro-mechanical parts as (sensor, motor drive, card, wheel, diaphragm, greaing, etc.), with all standard modification, re install it to fit their position, testing for ensuring fast response time and effective torque. | ea. | 2
total
Grand Total
| Estimated duration | n° of calendar days