## BoQ
The International Committee of the Red Cross
WATER & HABITAT DEPARTMENT
Raja / School / Rehabilitation
Al Raja Secondary School for Girls
Markaz / Ramadi / Anbar Governorate
2017-05-23
Raja / School / Rehabilitation
Markaz / Ramadi / Anbar Governorate
Al Raja Secondary School for Girls
Item | Description | Unit | Qty | Unit Price (USD) | Total Price (USD)
A | Civil Works
A.1 | Site clearance: Provision of materials and work to clearing the site, includes removing all dirt, deprise according to the direction of ICRC engineer. | ea. | 1
A.2 | Roof mastic of the existing building: Provision of materials and work to replace the old roof tile' mastic, the work includes cleaning the joints and apply new one, fill the joints with mastic and pressed or ironed with hot steel swefal. | m2 | 330
A.3 | Roof finishing: Provision of materials and work to dismantle the existing damaged roof finshing, the roof must be cleaned thoroughly, 2 layers of prime coats to be applied in opposite directions, 2 layers of liquid tar in hot condition to be applied in opposite directions, 2 bituminous felt have to be laid in opposite direction, clean river soil free from dirt, roots and other matters to be spread over the water proofing layers taking care of the required slopes, concrete tiles of (80 x 80) cm to be cladded on the leveled soil, then the joints between the concrete tiles (stigers) to be filled with mastic and pressed or ironed with hot steel swefal. All these details to be implemented as per the technical specifications and instructions of ICRC engineer, the work includes the removal of old existing roof details. (or bad slope) stigers and reconstruct the roof finishing to correct the existing damaged slope to make the job complete in every part and details. | m2 | 1100
A.4 | Building of 36 cm wall: Provision of material and building of 36 cm thick rock walls using good rock of sharp edges with cement mortar, all rock works should be of an even face. The work includes, the damp proof course (D.P.C) of (15 cm) thick using concrete mix 1:2:4 with a suitable water proofing material and with all needed shuttering. Accuracy must be taken during implementation, required connect with existing wall and demolish the damaged walls. | m3 | 60
A.5 | Reinforced Concrete Work: Provision of materials and work to cast in situ a reinforced concrete for (slab, beams, lintels, shade over the windows, and parapets, height of the parapets and concrete thickness to be according to the existing) This includes reinforcement steel bars, shuttering with all needed requirements as per the technical specifications, and according to the ICRC Engineer's instructions. | m3 | 40
A.6 | Build fence: Provision of materials and work to build fence ( height and thick smilare to the existing) using concrete block and cement mortar and leave interval expansion joint each 10m length . The work includes: demolish the exist affected fence and remove the debris away the site, cement plastering and flash cement pointing for both sides similare to the existing. | ml | 20
A.7 | Gypsum plastering : Provision of materials and work to plaster the walls & ceilings, by using gypsum and plaster of Paris in a very good way without leaving any lines or marks to obtain a smooth surface; the work includes removing the existing damaged plaster when its need | m2 | 1300
A.8 | Cement plastering: plastering of external walls by using cement mortar. The final face should be suitable to receive flash cement pointing | m2 | 950
A.9 | Flash Cement Pointing: Provision of materials and work to finish the final face of facade with flash cement pointing. The type and colour is to be decided by the Engineer. | m2 | 670
A.10 | Skirting: Provision of materials and work to make a skirting by using ceramic tiles 10 cm in height .The skirting will be fixed by using cement mortar. Care must be taken in implementing the work. | ml | 300
A.11 | Stair: Provision of material and work to demolish the existing damaged steps cover, and supply new steps (tread) of 3 cm thick completed with riser 2cm thick of precast type, the work includes the cement morter, the corection of the concrete steps level and the required fixation of the seps | ea. | 16
A.12 | Walkways: Provision of material and work to demolish the existing damaged concrete layer of the walkways and construct new 10 cm concrete thick, using SR cement. | m2 | 100
A.13 | Doors: Supply and install, door completed with frame . The work includes using all suitable sections similar to the existing (new sections). All doors will have suitable switch locks, hinges, handles, and required paint . also the work include demolish the existing damaged door
A.13.1 | Wooden doors of dimensions (1 m X 2.1m) | ea. | 13
A.13.2 | Aluminum door, of 2.10m X0.8m for bathrooms | ea. | 1
A.13.3 | Steel door, of dimensions (1 m X 2.1m) | ea. | 41
A.13.4 | Steel door, of dimensions (1.5m X 2.25m) | ea. | 1
A.13.5 | Steel door, of dimensions (2.0m X 2.5m) | ea. | 1
A.13.6 | Steel door, of dimensions (3.6m X 2.25m) | ea. | 1
A.14 | Windows (new):Supply, install and erect Steel windows of new sections similar to the existing, with all hinges, bolts, glass, (where required, according to ICRC engineer instruction), and handles to make the job complete in every part and detail, also demolish the existing damaged windows | m2 | 150
A.15 | Windows (repair):Provision of material and work to maintain, repair and operate the existing damaged Steel windows and doors (where required, according to ICRC engineer instruction), the works includes hinges, bolts, glass, mosquito gauze and all the missing parts. | m2 | 90
A.16 | Mosaic tiles: Provision of materials and work to clad floors with mosaic concrete tiles (dimensions similar to existing), to replace the damaged tiles, using cement mortar all; joints must be filled with white cement mixed with filler powder to fill joints. All materials should be quality controlled, the work includes remove the existing damaged floor details. | m2 | 250
A.17 | Painting (internal): Provision of materials and work to Paint the ceilings and walls inside the building of al Marjan quality, Plastic Paint for the internal walls the work includes the Preliminary coat. | m2 | 4500
A.18 | Painting (external): Emulsion paint of 3 coats for the external walls, includes the oil paint for the steel grills of the windows | m2 | 7500
A.19 | Shade for walkways : Provision of materials and work to manufacture and erect new shade with external dimensions similar to the existing, using galvanized steel columns of 3" dia. and corrugated galvanized steel sheets of gauge 22 to be fixed by means of hooks with the steel structure of angle section beam of (2.5" X 2.5" X 3/8") and hollow pipe of (2" X 4"). Work includes painting the steel structure with one layer of anticorrosion paint then three layers of oil paint of good quality. | m2 | 120
Total
B | Sewage, sanitation and plumbing Works
B1 | Sewage system: Provision of material and work to clean the existing septic tank and the associated tanks, the work includes pumping out the septic tank and haul away the waste to an approved treatment and processing facility. Clean all the existing inspection manholes and open the clogging pipes, maintain and operate the existing rain water pipes, also replace the damaged manhole cover and supply the missing manholes covers. | ea. | 1
B2 | Rain Water Drain Pipes: Provision of materials and installation of new PVC drain pipes. The work includes supplying and erecting all drain pipes of 3" and 4" in dia similar to the existing. with all accessories and fittings required, closing all openings by using cement with a suitable binding agent. | ml | 140
B3 | Water cistern: Provision of material & works to supply install new water cistern, wall mounted with all accessories required for installation. The contractor is requested to submit samples of good quality, fittings and accessories…etc, to get ICRC Supervising Engineer acceptance, work includes demolish the existing damaged cistern. | ea. | 10
B4 | Water pipes: Provision of material and work to supply, install connect and test galvanized steel water pipes of following nominal diameters for outside main building pipes and polypropylene water pipes for cold and hot water inside the building to replace the existing damaged pipes
B4.1 | Of (1/2") Dia. | ml | 12
B4.2 | Of (3/4") Dia. | ml | 25
B5 | Water tap: Provision of material and work to supply and install new Water tap of good quality, work includes the required, fittings and accessories…etc. | ea. | 30
B6 | Water tank: Provision of materials and work to supply, install and connect new PVC water storage tank of (1m³) capacity, along with the needed accessories, over flow, cover | ea. | 14
Total
C | Electrical Works
C1 | Main control panel: Provision of materials and work to maintian and repair the existing main control panel, The work includes replace all the damaged MCCBs , all the necessary wiring, indication lamps, Ammeters, voltmeter with selector switch, required bus- bars, terminals, cable glands and fixation, All the electrical provided materials, should be brand new and of western origin. | ea. | 1
C2 | Branch distribution board:Provision of materials and work to supply and install, Branch distribution board 3 PH of main isolator (100 A) and 12 lines .the work includes wiring, connection, fixation and load balance all supplied component should be western origin. Note: - All the existing electrical conduits inside the walls should be protected during the demolishing works, and to be used for the new wiring. - All the electrical wiring should be extended through electrical conduits and trunking., all the existing damaged electrical conduits and accessories should be removed out of the site. | ea. | 2
C3 | power cable: Provision of materials and work to supply, install and connect power cable of size (4 X 50 mm2) , the work includes all the accessories of terminals, cable tray,fixation, and connection | ml | 65
C4 | Internal light: Provision of materials and work to supply and install, economic lamp (2X22 watt) to be fixed in the false ceiling, the work includes, cable of 2x1.5mm2, wiring, connection, switches and fixation. | ea. | 220
C5 | Outdoor light: Provision of materials and work to supply and install weatherproof outdoor type (250 W) Sodium bulb light projector complete with frame, the work includes necessary wiring (2 X 2.5 mm2), CB of 20 A for each 2 projectors and switch | ea. | 14
C6 | Electric bell: Provision of materials and work to supply and install electric bell completed with frame, the work includes necessary wiring (2 X 1.5 mm2) and switch | ea. | 2
C7 | Water boiler: Provision of materials and work to install brand new electrical water boiler of capacity 80 liters of a good quality, the work includes all needed water supply piping, outlet piping connections, power cable of 2x4mm2, earth cable of 1.5mm, piping and piping modification, accessories with all electrical works needed to complete the job. | ea. | 2
C8 | Exhaust fan: Provision of material and work to supply, install, connect and operate exhaust fan (12") Diameter of best quality, The work includes all the required wiring, cable 2x1.5mm and fixation. | ea. | 10
C9 | Ceilling fan: Provision of materials and work to supply and install of brand new electrical ceilling fan of a good quality, to be fixed with the false ceilling , work includes power cable of 2x2.5mm2, earth cable of 1.5mm, accessories with all electrical works needed to complete the job. | ea. | 40
C10 | Water pump: Provision of material and work to supply, install and operate a new water pump of 1", western origin, (H=27m, Q=5 m3/h), 1450 RPM. The work includes all needed piping, gate valve, unions, non return valves & cable of 3X2.5mm, electrical wirings and earth connection, control panel to switching between in use and stand by pump, to be mounted on concrete with protection steel cage. | ea. | 2
C11 | Power socket: Provision of material and work to supply, install and operate a new power socket. electric load should be distributed in the branch distribution board phases
C11.1 | of 15A, using (2 X 4 mm2) feeding wires and earth wire of (2.5 mm2). | ea. | 20
C11.2 | of 13A, using (2 X 2.5 mm2) feeding wires and earth wire of (1.5 mm2), | ea. | 50
Total
D | Backup generator
D.1 | Provision of material and work to supply, install, connect and operate brand new generator (Assembled in Lebanon), with sound proof cabinet) Perkins engine type of (45) kVA Prime, the work includes , transportation, loading, unloading to site, all required electrical connections, operational materials e.g. batteries, oil, filters, etc., with testing and operating, according to the technical specification. | ea. | 1
D.2 | Shade for generator : Provision of materials and work to manufacture and erect new shade with external dimensions of (3m X 4m, 3m height), to protect the generator, using galvanized steel columns of 3" dia. and corrugated galvanized steel sheets of gauge 22 to be fixed by means of hooks with the steel structure of angle section beam of (2.5" X 2.5" X 3/8") and hollow pipe of (2" X 4"). Work includes painting the steel structure with one layer of anticorrosion paint then three layers of oil paint of good quality. | m2 | 12
Total
E | Water purification unit
E.1 | New Water Cooler with Water Purification Unit: Supply, install, connect and test new water coolers of best quality, Hasawi - Kuwaiti brand, UGUR - Turkish brand, or equivalent, of 2 taps. The price includes supply of new water purification unit for each water cooler, WPU of three series filters, one cellulose & two carbon filters with UV system, of best quality with a capacity of (60) L/h, to be installed on the wall inside suitable protection box and connected with the water piping network to supply treated water for the water cooler. The work includes all materials needed to complete the job and to make the system run properly (fixation, valves, electrical power supply with protection device & connections….etc.). | ea. | 4
Total
Summary
A | Total amount for Civil works
B | Total amount for Sewage, sanitation and plumbing Works
C | Total amount for for Electrical Works
D | Total amount for Backup generators
E | Total amount for Water purification unit Works
Grand Total USD
| Duration | n° of calendar days