## Sheet1
The International Committee of the Red Cross
WATER & HABITAT DEPARTMENT
Shamsiyat / WTP / Rehabilitation
Shamsiyat village / Hamdaniya / Nainawa
20 - June - 2017
Shamsiyat / WTP / Rehabilitation
Shamsiyat village / Hamdaniya / Nainawa
No. | Item Description | Unit | Estim Qty | Unit P. (USD) | Total Price (USD)
A | Construction operators room, W.C, Alum & chlorine rooms
A.1 | Supplying materials and providing manpower to clean the site of the project and removing all the debris of the damaged building and the damaged pipes, fittings and electrical cables and other equipment's. The debris should be transported outside the village. | L.S | 1
A.2 | Leveling the ground & planning according to drawings | M² | 50
A.3 | Casting foundation 50*40cm using reinforcement concrete C25, 6 steel bars 5/8" c/c and stirrup 3/8" 20 cm, with all necessaries for work with back filling & compacting | M³ | 10
A.4 | Building the walls with concrete block and cement mortar for 3 m height | M³ | 26
A.5 | Casting the roof and the lentils over the windows, doors and the walls using C25 concrete Rcc two layers 12 mm bars, with all work demands & well curing. | M³ | 12
A.6 | Plastering by cement mortar ,inside & outside with good smoothing then paint, by paint lite (Turkish) 3- layers | M² | 225
A.7 | Supply & install ceramic tiles for walls of W.C & its corridor , | M² | 30
A.8 | Supply & install PVC doors 2.10*1m good quality | PCS | 4
A.9 | Supply & install PVC windows 2*1.2 good quality with 4mm glasses | PCS | 4
A.10 | Supply & install PVC window 0.5*0.5 m movable with 6" ventilator good, quality & 6mm glass | PCS | 1
A.11 | Casting the floor using concrete C25 with good smoothing and 15 cm thickness, the work includes coating the floor with mosaic tiles 40*40 cm with the grinder and filling the joints with cement. | M² | 45
A.12 | Concrete for entrance and walkway. Supply materials and casting plain concrete (1:2:4), 15 cm thickness with one layer of BRC 6mm dia., 20x20 cm opening, expansion joints at 2.5 m.The price includes grading, leveling, well compaction of the foundation soil, laying 10 cm thickness well compacted crushed stone and smoothening the surface of concrete, wood blocks used for joints should be mechanically smoothened. | M2 | 22
A.13 | Supplying materials and building the fence for the whole project 100 m length and 2.2 m height with concrete block and cement mortar, the work includes foundation of reinforced concrete (30 cm depth, 60 cm width) with 6 no. of 12 mm bar and 10 mm stirrups at 25 cm, with the excavation. The work includes as well plastering withe cement mortar and painting with emulsion paint, making expansion joints each 6 m. | M³ | 55
A.14 | Supplying materials and installing metallic sliding door of dimensions 3x2 m with plate gage 18 and one face for the entrance of the project, including painting with anti corrosion paint and oil paint, with suitable lock according to the engineer instructions and the attached drawings. | No. | 1
A.15 | Supply & install water tank 1m3 1.2mm with float valve & 3/4" PVC pipe to water supply . | PCS | 1
A.16 | Supply & install wash basin ceramic 40*60cm complete with mixer, piping ,valves, fixing ----etc. | PCS | 1
A.17 | Supply & install water tapes with its connections ( steel type) | PCS | 2
A.18 | Supply & install eastern WC seat ceramic type with 4" gully & 4" pipe to the S.T. through M.H. 40*40cm, flash & accessories | PCS | 1
A.19 | Septic Tank: Construction of septic tank of size (3x3x2) m. All inclusive excavation, crushed stone, plain concrete, walls from solid concrete blocks 15x20x40 cm, all with cement mortar, plastering, reinforced concrete, three cast-iron covers each (60x60) cm with frame, shuttering, etc. with all necessary work according to the attached details. The price includes installation of ventilation galvanized pipe size 3" – 5 meter high passing through the nearest fence with the elbow of screened cup at the top to be properly fixed. | PCS | 1
Electrical works: Supply & install electrical lights & sockets points using wires 2*1.5& 2*2.5mm
A.20 | a- Water Proof florescent 40 w good quality | PCS | 8
A.21 | b- Water Proof fitting with 25 w bulb | PCS | 4
A.22 | c-Ceiling fan good quality with all accessories. | PCS | 3
A.23 | d- Secondary distribution boards S.D.B 24 lines with main circuit 100 Amp. | PCS | 1
A.24 | Supply & install cable 2*10mm for main supply | M.L | 20
A.25 | Supply, install, and connect AC split unit (indoor, 2 tons, 18’000 BTU/hr, cooling and heating, type general Max or equivalent type available in the local market), the works includes all the fittings, base for the compressor and the labors to do the opening for the units inside the walls of the cells. requirements cables and circuits breaker needed to complete the work. The electrical connections of the AC split units should be from outside the building. | No. | 1
A.26 | Supply & install electrical heater boiler 120 lt ,3000 W good quality with all the fittings, pipes and valves needed. | LS | 1
Sub-Total A
B | Mechanical works
B.1 | High lift pumps:- Supplying materials and providing the required equipment, labor and tools for installing and operating brand new set horizontal pump (Split case type, Turkish made, contractor shall submit technical specifications of alternative and submit the catalogs of the pumps and will provide a supplier’s pump efficiency curve for each pump requested, to ensure that the pumps installed are efficient and not simply matching the requested flow rate and head). Complete set, Electrical Motor and suitable Starter). The specification of the Pump: Electrical motor, 380 VAC Y/D, 50 Hz. Q = 50 M³/hr & H = 60 m, RPM=1450. Shaft: stainless steel. Work & Price include; supplying and installing suitable new (integrated control panel of ABB components or equivalent) inside the station, with all required & related electro-mechanical connections as standard to achieve neat performance. The work should includes dismantling the old pumps and replacing the new. Note: The work should include supplying and installing suitable starters to the two existing high lift pumps (Q=50 m3/h, 60 m). | No. | 2
B.2 | Supplying and installing new brand cast iron gate valve DN 150, PN16 for the suction and delivery side, working temperature (-10 to + 110), hand wheel type, stem should be stainless-steel, wedge should be ductile iron rubber coated, casket EPDM- NBR (Ethylene propene, Nitrile, Fluorine (Viton)), western origin, flange type, with all bolts and nuts. The work includes providing any fittings required or any pipe modification and paint all with Jotun paint. | No. | 4
B.3 | Supplying and installing new brand cast iron check valve DN 150, PN16, working temperature (-10 to + 110), hand wheel type, stem should be stainless-steel, wedge should be ductile iron rubber coated, casket EPDM- NBR (Ethylene propene, Nitrile, Fluorine (Viton)), western origin, flange type, with all bolts and nuts. The work includes providing any fittings required or any pipe modification and paint all with Jotun paint. | No. | 2
B.4 | Low lift pumps for the extension WTP:- Supplying materials and providing the required equipment, labor and tools for installing and operating brand new set horizontal pump (Split case type, Turkish made, contractor shall submit technical specifications of alternative and submit the catalogs of the pumps and will provide a supplier’s pump efficiency curve for each pump requested, to ensure that the pumps installed are efficient and not simply matching the requested flow rate and head). Complete set, Electrical Motor and suitable Starter). The specification of the Pump: Electrical motor, 380 VAC Y/D, 50 Hz. Q = 100 M³/hr & H = 20 m, RPM=1450. Shaft: stainless steel. Work & Price include; supplying and installing suitable new (integrated control panel of ABB components or equivalent) inside the station, with all required & related electro-mechanical connections as standard to achieve neat performance. The work should includes dismantling the old pumps and replacing the new. Note: The work should include supplying and installing suitable starters for existing low lift pump (Q=100 m3/h, 20 m). | No. | 1
B.5 | Supplying and installing new brand cast iron gate valve DN 200, PN16 for the suction and delivery side, working temperature (-10 to + 110), hand wheel type, stem should be stainless-steel, wedge should be ductile iron rubber coated, casket EPDM- NBR (Ethylene propene, Nitrile, Fluorine (Viton)), western origin, flange type, with all bolts and nuts. The work includes providing any fittings required or any pipe modification and paint all with Jotun paint. | No. | 2
B.6 | Supplying and installing new brand cast iron check valve DN 200, PN16, working temperature (-10 to + 110), hand wheel type, stem should be stainless-steel, wedge should be ductile iron rubber coated, casket EPDM- NBR (Ethylene propene, Nitrile, Fluorine (Viton)), western origin, flange type, with all bolts and nuts. The work includes providing any fittings required or any pipe modification and paint all with Jotun paint. | No. | 1
B.7 | Rehabilitation the existing pressure filters: Supplying materials and technicians & overhauling, repairing of the existing pressure sand filters horizontal type, rated flow (14m3/m2/h) diam 2.3m, length 6 m (dish/dish), dish end, the shell thickness 10 mm, end dish 12 mm and nozzles plate (baffle)14mm, carbon steel (ST-37) made, the work includes fixing and replacing any damaged parts and repaint by epoxy paint from inside and oil paint from outside, supplying of HDPE nozzles, 55 nozzles per square meter of the baffle if needed, pressure gauges 10 bar. Checking the nozzles plate and to be replaced if it is damaged with supporting it from bottom. Supplying and lying-in media materials consists of different layers according to the Standard. 1-Coarse grade (9.5-13)mm. 2-Medium grade (6.5-9.5)mm. 3-Fine grade (2.5-6.5)mm. The price also includes replace the damaged valves by new automatic and manual valves, replacing the casket of the inspections manholes, drain, pipes and all fittings & civil works needed, to be tested according to required technical specifications and instructions of ICRC engineer. | No. | 1
B.8 | Rehabilitation the existing pressure filters: Pressure Filters: Supplying materials and technicians & overhauling, repairing of the existing pressure sand filters vertical type, rated flow, diam 1.9 m, height 2.5 m (dish/dish), dish end, the shell thickness 10 mm, end dish 12 mm and nozzles plate (baffle)14mm, carbon steel (ST-37) made, the work includes fixing and replacing any damaged parts and re-paint by epoxy paint from inside and oil paint from outside, supplying of HDPE nozzles, 55 nozzles per square meter of the baffle if needed, pressure gauges 10 bar. Checking the nozzles plate and to be replaced if it is damaged with supporting it from bottom. Supplying and lying-in media materials consists of different layers according to the Standard. 1-Coarse grade (9.5-13)mm. 2-Medium grade (6.5-9.5)mm. 3-Fine grade (2.5-6.5)mm. The price also includes replace the damaged valves by new automatic and manual valves, replacing the casket of the inspections manholes, drain, pipes and all fittings & civil works needed, to be tested according to required technical specifications and instructions of ICRC engineer. | No. | 2
B.9 | Rehabilitation the Sedimentation tank: Supplying materials and technicians & overhauling, repairing of the existing of Sedimentation tanks, the specifications of the tanks: two tanks of Width 2.44 m, Length 12.40, Height 2.44 m. The work consists of cleaning the inside of the tanks and re-painting by epoxy paint from inside and oil paint from outside. Including supplying and fixing Lamella sheets packs, each with adequate number of individual plates inclined at 55° to vertical, to provide total effective surface area of 252 m2 per Compartment. Plate Spacing: 25 mm (Nominal). Materials of Construction: GRP or Epoxy CS plates (or similar). Each individual plate pack assembly will be removable with the use of a small crane or similar lifting device. The work includes as well replacing the damaged high and low mixing parts with the vertical shafts. Replacing all the damaged valves, drain pipes and other fittings. | Set | 1
B.10 | Chlorine System (powder chlorine) : - a. Chlorine Feed Pump Quantity : 1 Max. Output Capacity : 100 lt/h b. Chlorine Tank Quantity : 1 Material : Polyethylene Capacity : 1000 liters Inlet / Outlet Connections : 15 mm (1/2") The work includes all required equipment's, fittings and all other necessary works. | Set | 1
B.11 | Alum Feed System (Flocculation with agitator) a. Aluminum Sulphate Preparation Tank Quantity : 1 Material : Polyethylene Capacity : 1000 liters Inlet / Outlet Connections : 15 mm (1/2") b. Aluminum Sulphate Preparation Tank’s Mixer Quantity : 1 Type : Fast Mixer Period : 350 d/d Power : 0,37 KW Mixer : Stainless Steel C. Chemical Feed Pump: Max. Output Capacity : 20 lt/h Max. Head : 10 bar | Set | 1
B.12 | Air system: Supplying materials and installing, testing and operating new air blower system, centrifugal type capacity 180 m3\hr, 200 mbar, RPM 1500 - 2900, with all necessary mechanical and electrical connections. Turkish origin (Silent Roots Blower). | No. | 1
B.13 | Supplying materials and constructing metallic shed to protect all the parts of the compact unit, the work includes supplying and fixing the columns 4" G.I pipes according to the attached drawings, supplying and fixing beams of squire pipes size 2"x4" and supplying and fixing ribbed plate sheets of gage 0.7 painted by thermal paint. All the iron parts of the shed should be painted by anti corrosion paint and three layers of oil paint. | M² | 200
Sub-total B
C | Electrical works
C.1 | Providing materials & fixing electrical distribution transformer (11/0.4 k.v, 250 KVA, working with stable voltage 400 V out door according to IEC 76 (Turkish, French or German made), including two electrical poles and all the fittings and cables for the connection. The work includes as well circuit of 800 amp with the board and should be ABB type. | No. | 1
C.2 | Main Control Panel: - Supplying, assembling and testing new control panel for all the electrical connections of the two projects, the price includes all the cables needed and the installation of the followings: - One main circuit breaker 600 AM for incoming supply with full protection. - Bas Bar 800 A complete set. - Digital gages multi readings. - MCCC 250 A (4 pieces). - MCCC 160 A (2 piece). - MCCC 60 A (3 piece). All the circuits should be of Schneider type Electrical components suitable for 380 V, 3 phase, 50 Hz, outdoors. The work also includes providing and installing all required fittings, electrical cables and all other requirements. The work includes all required cables (color coded and numbered cabling), fittings, accessories. making complete anti lighting system by using cupper bars/wire of 50 mm with all connections to the plant from inside & outside, electrical connection with the existing power supply source in the area and all other necessary works to put all the plant equipment's in full operation capacity. | No. | 1
C.3 | External Illumination: - Providing, installing and operating lighting system (projectors 400 watt of sodium tv type with steel columns/poles 1.5" dia) with starters, cables, photo cells, switch boards and connecting them with power source. | No. | 6
C.4 | Supplying and fixing cable size (4x35) mm² to connect the low lift pumps from the intake structure to the main control panel at the CU location, the laying of the cable should be according to supervisor Eng. Instructions | M.L | 200
C.5 | Supplying and fixing cable size (4x50) mm² to connect the intermediate pumps to the main control panel with the circuit 250 Amp, the laying of the cable should be according to the supervisor Eng. Instructions. | M.L | 150
C.6 | Supplying and fixing cable size (4x10) mm to connect the alum, chlorine systems, the motors of the mixers and the lighting system to the main control panel, the laying of the cable should be according to the supervisor Eng. Instructions | M.L | 100
C.7 | Supplying materials and installing generator (Perkins type-AC 400-3 phases-50 Hz) of 125 K.V.A capacity with following specifications: Engine: 1. Perkins heavy duty diesel engine. 2. Four cycle, water cooled, turbo charged. 3. Electronic governor control system. 4. Direct injection fuel system. 5. 4 valves per cylinder. 6. Industrial capacity and steel below. 7. cooling radiator and fan. canopy. Alternator: 1.Burshless, single bearing system, 4 poles. 2. Self-exciting and self-regulating. 3. Solid state Automatic voltage regulator. The price includes all the cables needed to be connected to the electrical system of the unit. | No. | 1
C.8 | Supplying materials and preparing the location of the generator. The work includes the followings: 1. Casting the foundation of the shed with reinforced concrete 1:2:4 ratio and 20 cm thickness. 2. Excavating for the foundation of the columns of the shed with the dimensions 50x50x50 cm. 3. Supply material and fixing G.I pipes 3" size of length 5 m as columns for the shed, the end of the columns should be welded by plate of 40x40 cm and thickness 4mm. 4. Supply material and fix ribbed sheet plates of dimension 1x6m and gage 16, the plates should be fixed by bolts with the angle section beams. | M² | 40
C.9 | Supplying materials, fixing and extending electrical cable of size 4x50 mm2 to connect the generator with the main board of the project and with the main source of the electrical grid line. | M.L | 50
C.10 | Supply and install steel storage tank for the fuel of the generator with capacity 2000 liter, the plate should be gage 16, the price includes painting with oil paint and constructing concrete base from solid blocks with height of 1 m and connecting the tank to the generator. | No. | 1
Sub-total C
No. | DESCRIPTION
A | Civil works works for the old and extension WTP
B | Mechanical works for the old and extension WTP
C | Electrical works for the old and extension WTP
TOTAL AMOUNT
The duration |  |  | Working Days |  | days