## BoQ
The International Committee of the Red Cross
WATER & HABITAT DEPARTMENT
Abu Jassra / CU / Rehabilitation
Abu Jassra/Wajihia/ Muqdadiya / Diyala
2017-05-25
Abu Jassra/Wajihia/ Muqdadiya / Diyala
Item | Description | Unit | Qty | Unit Price (USD) | Total Price (USD)
1 | suction system
1.1 | Provision of materials and work to supply, and connect new suction galvanized steel pipe of (6") , the work includes the required fittings , the required accessories (flanges, elbows, reducer, etc.) also cutting ,welding, demolition of concrete bit , painting and all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | m.l | 10 |  | 0
1.2 | Provision of materials and work to supply and install a new foot valve (6") to the suction pipes, the work includes cutting, welding, painting and all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | ea | 2 |  | 0
1.3 | Supply, install and operate new gate valves (8" ) with all accessories , all the rubber washers , all piping modification and according to the instructions of the ICRC Engineer | ea. | 1 |  | 0
| Total |  |  |  | 0
2 | low lift system
2.1 | Provision of material and work to make the job complete in every part and details to supply, install and connect new horizontal pumps (End suction type, Electrical Motor, Star delta starter, Base plate and Guard) of Q = 50 m3/h, H = 20m, western origin with BRONZE IMPELLER The work includes, dismantle the existing damaged pump,the work includes installing new suction and delivery pipes 6" according to the instructions of the ICRC engineer with all the accessories (reducer ,anchor bolt, rubber washers, flanges, pressure gauges, connection cables, necessary pump alignment , fixation, testing and commissioning). The new LL Pump shall be connected to the new control panel and starter with a proper length of cable , with all the requirements to achieve a proper and neat performance according to the instructions of the ICRC Engineer. Testing and successfully operating are included in the price. | ea | 2 |  | 0
2.2 | Supply, install and operate new Butterfly valves of (4" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea | 4 |  | 0
2.3 | Supply, install and operate new non return valves of (4" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea | 2 |  | 0
2.4 | Supply, install and operate new Flexible Joint of (4" ) with all accessories , the works including all the rubber washers and all piping modification. | ea | 2 |  | 0
| Total |  |  |  | 0
3 | High lift system
3.1 | Provision of material and work to make the job complete in every part and details to supply, install and connect new horizontal pumps (End suction type, Electrical Motor, Star delta starter, Base plate and Guard) of Q = 50 m3/h, H = 50m, western origin with BRONZE IMPELLER The work includes, dismantle the existing damaged pump ,the work includes installing new suction and delivery pipes 6" according to the instructions of the ICRC engineer with all the accessories (reducer,anchor bolt, rubber washers, flanges, pressure gauges, connection cables, necessary pump alignment , fixation, testing and commissioning). The new HLP shall be connected to the new control panel and starter with a proper length of cable , with all the requirements to achieve a proper and neat performance according to the instructions of the ICRC Engineer. Testing and successfully operating are included in the price. | ea | 2 |  | 0
3.2 | Supply, install and operate new Butterfly valves of (4" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea | 4 |  | 0
3.3 | Supply, install and operate new non return valves of (4" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea | 2 |  | 0
3.4 | Supply, install and operate new Flexible Joint of (4" ) with all accessories , the works including all the rubber washers and all piping modification. | ea | 2 |  | 0
| Total |  |  |  | 0
4 | settling tank
4.1 | Provision of material and work to repair and operate the settling tank ( 6m x 2.4m x 2.4m) The work includes completely washing and cleaning the walls and bottom using electric steel brush to clean rust area , removing all the accumulative sludge and heavy stacks of mud, cleaning and unclogging the sludge discharge pipes, repairing any defected parts in internal and external walls, bottom, and repairing any leakage points, replace the damage and missing steel plates in order to restore the tank as per its original design, including replacing the damaged bracing iron angle, painting with (2) layers of food grade epoxy paint for the internal walls and externally with suitable oil paint after prime painting of anti-rust with all requirements to complete the job perfectly and all the works must be according to instructions of ICRC engineer | ea | 1 |  | 0
4.2 | Supply, install, connect and operate new flash mixer of capacity (1.5 kW, 220 V, 1000 rpm) including stainless steel shaft and propeller to replace the defective one. The work includes making proper modification to fix the equipment accurately on its position with all electromechanical connections (cable, protection steel frame, etc.) to implement the job neatly as standards. | ea. | 1 |  | 0
4.3 | Supply, install and operate new Butterfly valves of (6" ) with 1 meter length of new galvanized pipe (6" ) to connect the settling tank to the HL Pumps , the works including all accessories of flange adapter, rubber washers , all piping modification,cutting ,and welding painting and all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | ea | 2 |  | 0
4.4 | Provision of material and work to maintain, repair and operate the piping network (6" ) of the CU with (elbow,T section, washers and all the accessories) the works including all piping modification,cutting ,welding ,painting and all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | LS | 1 |  | 0
| Total |  |  |  | 0
5 | pressure filters
5.1 | Provision of material and work to maintain, repair and operate the vertical pressure filters (cylinder shape 1.8m x 1.5m ), the work includes replace the vent relef valve , repair the leakages, required welding of the nozzle base plate and fixed support, maintain and cleaning the filter (internally), coating the internal side with two layers of food grade epoxy and externally with suitable oil paint after the red oxide prim, supply and install nozzles , replace the defected or improper parts with new ones such as (washers, manometer gauge, bolts.), the work include all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | ea | 2 |  | 0
5.2 | Provision of material and work to supply and laying filter media materials consists of different layers according to the Iraqi general DoW Standard. As below: 1-Coarse grade (9.5-13)mm , Height of 10 cm 2-Medium grade (6.5-9.5)mm , Height of 10 cm 3-Fine grade (2.5-6.5)mm , Height of 10 cm 4-Sand quartzes (0.6-0.65)mm , Height of 60 cm with laboratory tests certification , and all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | m3 | 3.5 |  | 0
| Total |  |  |  | 0
6 | chemical units
6.1 | a-ChlorineaUnit Provision of material and work to supply and install brand new Chlorinators of western origin (dosing equipment) wall mounted, of a capacity of (1Kg/h), ALLDOS type. The work includes the necessary fixation of the injector and the dosing device, supply, install and connect PVC pipe of 1" of a required length, all necessary fittings and strainer, non-return valve. the work also includes the connection with the injection point on the discharge pipe in addition to the injection points of pre-chlorination in the settling tank with all required PVC piping and valves to control the dosing amount through both the pre-chlorination point and the delivery pipe, required frame and base, the price also include testing and operating the chlorinators functionally and successfully. | ea | 1 |  | 0
6.2 | Provision of material and work to supply, install and operate Chlorinator Boosting Pump (Q=2m3/h, H=80m) western origin, the work include the electrical starter (1.5KW), electrical connection, supply and connect PVC and GS piping network with all the necessary fittings ,and all the requirements to complete the job perfectly and all the works must be according to instructions of ICRC engineer | ea | 1 |  | 0
6.3 | b-Alum Unit Provision of material and work to supply and install brand new Alum system consist of the following : 1. Alum tank : PVC heat resistant solution preparation tank of (1000 L) 2. dosing pump : 50 L/h, H = 40m V = 3ph , 380Volt pressure 4 bar 3. Alum mixer Power 0.5kw V= 3Ph , 380 Volt with speed gear box 1500rpm to 180rpm , 0.9 m length stainless steel shaft, and propeller The work includes supply and install all the required galvanized and PVC piping,fittings , flexible hose, wiring, cables, control panel for the system ,accessories,and all the requirements to complete the job perfectly and all the works must be according to instructions of ICRC engineer | ea | 1 |  | 0
| Total |  |  |  | 0
7 | Back up Generator
7.1 | Provision of material and work to supply, install, connect and operate brand new generator Perkins engine type of (75) kVA Prime, the work includes , transportation, loading, unloading to site, all required electrical connections, operational materials e.g. batteries, oil, filters, etc., with testing and operating, according to the technical specification. | ea | 1 |  | 0
7.2 | Provision of materials and work to supply , install and connect (to the generator )a G.S fuel storage tank of (1000L) on proper steel frame the work include pipes fittings ,valve ,level gauge and all requirements to make the job complete and according to the instructions of the ICRC Engineer. | ea | 1 |  | 0
7.3 | Provision of material and work to Supply, install, connect and test new manual transfering switch of 250 Amps, to be fixed inside suitable box. Work includes all connections,cables and accessories and all requirements to make the job complete and according to the instructions of the ICRC Engineer. | ea | 1 |  | 0
7.4 | Provision of materials and work to make the job complete in every parts and details to supply and install (main control panel), The main control panel should have a brand new insulated cabinet of (IP 55), main MCCB of (250 A) No.1, 100 A No.2, 75A No.2, and 10 A No.10 . the starters of ( flash mixter, dosing pump, Alum mixter ) fit to their capacities, (starters of HLP , LLP and boosting pump are already supplied by items 2.1 ,3.1 and 6.2 ) phase failure and over under voltage protection device, The works includes all the necessary wiring, indication lamps, Ammeters, voltmeter with selector switch, terminals, cable glands and fixation, the required C.B, Bus bars, all requirements to make the job complete and according to the instructions of the ICRC Engineer.the price also include operating and Testing. | ea | 1 |  | 0
| Total |  |  |  | 0
8 | Civil and External Illumination
8.1 | Provision of materials, labors, tools and equipment to renovate the existing operators room (4.5 X 4.5 m) and the bathroom (4.5 X1.5 m), maintain the doors and windows replacing any defective part (steel section and classes) with painting the inner and outer walls after proper repairing, supply and install new 2 no. of fluorescent light (4 feet ),2 base light units, washbasin, rearrange, repair the electrical wires,power switch repair the plumbing network, all the works must be according to instructions of ICRC engineer | Ls | 1 |  | 0
8.2 | Supply materials, tools and manpower to paint external walls of (22 X 19 X Height of 2m ) with two layers of emulsion paint then one layer of oil paint . technical details and selection of the colors as per the instructions of the ICRC Engineer | M2 | 350 |  | 0
8.3 | Provision of material and work to maintain, repair and operate the existing main gate, the works includes hinges, bolts, all the missing, damaged parts and the required oil paint of . | ea | 1 |  | 0
8.4 | Provision of material and work to maintain, repair , operate and paint the lighting poles, then supply and connect lighting lamps 400 watt white color , internal wiring connection (2 * 2.5) mm , starters, , switch boards and connecting them with power source ,accourding to the technical specifications and under instruction of ICRC engineer. | ea | 4 |  | 0
8.5 | Provision of materials and work to rehabiltite the existed protection sunshade with external dimensions of the back up generator (7m X 5m, 3m height) , work include replace the damage corrugated galvanized steel sheets ,and painting the steel structure with one layer of anticorrosion paint then three layers of oil paint of good quality. | M2 | 35 |  | 0
8.6 | Provision of materials and work to) rehabiltate and extend the protection shade for the CU of (9m X8m, 3m height), work include replace the damage corrugated galvanized steel sheets ,and painting the steel structure with one layer of anticorrosion paint then three layers of oil paint of good quality. | M2 | 72 |  | 0
| Total |  |  |  | 0
| Grand Total |  |  |  | 0
| Estimated duration | n° of calendar days