## BoQ
The International Committee of the Red Cross
WATER & HABITAT DEPARTMENT
Titin and Thabatia / CU / Rehabilitation
Hibhib/ Khalis / Diyala
2017-05-09
Hibhib/ Khalis / Diyala
Item | Description | Unit | Qty | Unit Price (USD) | Total Price (USD)
1 | Site Preparation
1.1 | Demolition and clean up the site: Provision of materials and work , tools, machineries and manpower to , demolition of the existed room , cleaning , removing all debris and rubble out of the site to make the job complete and according to the instructions of the ICRC Engineer. | Ls | 1 |  | 0
| Total |  |  |  | 0
2 | Suction System
2.1 | Supply materials and manpower to construct intake structure to be used steel I beams thickness of 12 inch and 8Inch with a steel (L beam ) thickness of 6 inches , 4 inches and the span walkway structure width not less than (1) m , 6 m length with U channel, walkway to be cover with Checker plate thickness (4mm) with fixing a handrail on both sides of the walkway structure. The handrail to be 1m height. The price includes painting all steel structure with 2 layers of antioxidant paint and 2 layers of oil paint, Item also includes install and fix the structure on the side of the river with a steel foundation and all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | ea | 2 |  | 0
2.1 | Provision of materials and work to supply, connect and extend new suction galvanized steel pipe of (6") , the work includes the required fittings , the required accessories (flanges, elbows, reducer, etc.) also cutting ,welding, demolition of concrete bit , painting and all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | m.l | 20 |  | 0
2.3 | Provision of materials and work to supply and install a new foot valve (6") to the suction pipes, the work includes cutting, welding, painting and all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | ea | 2 |  | 0
| Total |  |  |  | 0
3 | Low Lift System
3.1 | Provision of material and work to make the job complete in every part and details to supply, install and connect new horizontal pumps (End suction type, Electrical Motor, Star delta starter, Base plate and Guard) of Q = 50 m3/h, H = 20m, western origin with BRONZE IMPELLER The work includes, dismantle the existing damaged pump,the work includes modification of suction and delivery pipes according to the instructions of the ICRC engineer with all the accessories (reducer ,anchor bolt, rubber washers, flanges, pressure gauges, connection cables, necessary pump alignment , fixation, testing and commissioning). The new LL Pump shall be connected to the new control panel and starter with a proper length of cable , with all the requirements to achieve a proper and neat performance according to the instructions of the ICRC Engineer. Testing and successfully operating are included in the price. | ea | 4 |  | 0
3.2 | Supply, install and operate new Butterfly valves of (6") with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea | 6 |  | 0
3.3 | Supply, install and operate new non return valves of (6" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea | 4 |  | 0
3.4 | Supply, install and operate new Flexible Joint of (6" ) with all accessories , the works including all the rubber washers and all piping modification. | ea | 4 |  | 0
| Total |  |  |  | 0
4 | High Lift System
4.1 | Provision of material and work to make the job complete in every part and details to supply, install and connect new horizontal pumps (End suction type, Electrical Motor, Star delta starter, Base plate and Guard) of Q = 50 m3/h, H = 50m, western origin with BRONZE IMPELLER The work includes, dismantle the existing damaged pump ,the work includes modification of suction and delivery pipes according to the instructions of the ICRC engineer with all the accessories (reducer, anchor bolt, rubber washers, flanges, pressure gauges, connection cables, necessary pump alignment , fixation, testing and commissioning). The new HLP shall be connected to the new control panel and starter with a proper length of cable , with all the requirements to achieve a proper and neat performance according to the instructions of the ICRC Engineer. Testing and successfully operating are included in the price. | ea | 4 |  | 0
4.2 | Supply, install and operate new Butterfly valves of (4" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea | 8 |  | 0
4.3 | Supply, install and operate new non return valves of (4" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea | 4 |  | 0
4.4 | Supply, install and operate new Flexible Joint of (4" ) with all accessories , the works including all the rubber washers and all piping modification. | ea | 4 |  | 0
| Total |  |  |  | 0
5 | Settling Tank
5.1 | Provision of material and work to repair and operate the settling tank ( 12m x 6m x 2.5m) The work includes completely washing and cleaning the walls and bottom using electric steel brush to clean rust area , removing all the accumulative sludge and heavy stacks of mud, cleaning and unclogging the sludge discharge pipes, repairing any defected parts in internal and external walls, bottom, and repairing any leakage points, replace the damage and missing steel plates in order to restore the tank as per its original design, including replacing the damaged bracing iron angle, painting with (2) layers of food grade epoxy paint for the internal walls and externally with suitable oil paint after prime painting of anti-rust with all requirements to complete the job perfectly and all the works must be according to instructions of ICRC engineer | ea | 2 |  | 0
5.2 | Provision of materials and work to supply and install drain valve (4"). The work includes all required material and tools, testing and operating. | ea. | 8 |  | 0
5.3 | Provision of materials and work to supply and install flocculator mixer complete with steel shaft and propeller (motor of 0.75 kw). The work includes all the required material and tools to install, cable connection, electrical starter,Testing and successfully operating are included in the price. | ea. | 2 |  | 0
| Total |  |  |  | 0
6 | Pressure Filters
6.1 | Provision of material and work to maintain, repair ,connect and operate the vertical pressure filters (cylinder shape 1.8m x 1.5m ), the work includes replace the vent relef valve , repair the leakages, required welding of the nozzle base plate and fixed support, maintain and cleaning the filter (internally), coating the internal side with two layers of food grade epoxy and externally with suitable oil paint after the red oxide prim, supply and install nozzles , replace the defected or improper parts with new ones such as (washers, manometer gauge, bolts.), the work include all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | ea | 2 |  | 0
6.2 | Provision of material and work to maintain, repair , connect and operate the vertical pressure filters (cylinder shape 2.7m x 1.5m ), the work includes replace the vent relief valve , repair the leakages, required welding of the nozzle base plate and fixed support, maintain and cleaning the filter (internally), coating the internal side with two layers of food grade epoxy and externally with suitable oil paint after the red oxide prim, supply and install nozzles , replace the defected or improper parts with new ones such as (washers, manometer gauge, bolts.) , the work include all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | ea | 2 |  | 0
6.3 | Provision of material and work to maintain, repair , connect and operate the filters wash up system , the work includes replace the valves , repair the leakages, required welding, painting externally with suitable oil paint after the red oxide prim, and all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | ea | 2 |  | 0
6.4 | Supply, install and operate new valves of (3" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification according to the instructions of the ICRC Engineer. | ea | 12 |  | 0
6.5 | Provision of material and work to supply and laying filter media materials consists of different layers according to the Iraqi general DoW Standard. As below: 1-Coarse grade (9.5-13)mm , Height of 10 cm 2-Medium grade (6.5-9.5)mm , Height of 10 cm 3-Fine grade (2.5-6.5)mm , Height of 10 cm 4-Sand quartzes (0.6-0.65)mm , Height of 60 cm with laboratory tests certification , and all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | m3 | 15 |  | 0
| Total |  |  |  | 0
7 | Chemical Units
7.1 | a-ChlorineaUnit Provision of material and work to supply and install brand new Chlorinators of western origin (dosing equipment) wall mounted, of a capacity of (1Kg/h), ALLDOS type. The work includes the necessary fixation of the injector and the dosing device, supply, install and connect PVC pipe of 1" of a required length, all necessary fittings and strainer, non-return valve. the work also includes the connection with the injection point on the discharge pipe in addition to the injection points of pre-chlorination in the settling tank with all required PVC piping and valves to control the dosing amount through both the pre-chlorination point and the delivery pipe, required frame and base, the price also include testing and operating the chlorinators functionally and successfully. | ea | 2 |  | 0
7.2 | Provision of material and work to supply, install and operate Chlorinator Boosting Pump (Q=2m3/h, H=80m) western origin, the work include the electrical starter (1.5KW), electrical connection, supply and connect PVC and GS piping network with all the necessary fittings ,and all the requirements to complete the job perfectly and all the works must be according to instructions of ICRC engineer | ea | 2 |  | 0
7.3 | b-Alum Unit Provision of material and work to supply and install brand new Alum system consist of the following : 1. Alum tank : PVC heat resistant solution preparation tank of (1000 L) 2. dosing pump : 50 L/h, H = 40m V = 3ph , 380Volt pressure 4 bar 3. Alum mixer Power 0.5kw V= 3Ph , 380 Volt with speed gear box 1500rpm to 180rpm , 0.9 m length stainless steel shaft, and propeller The work includes supply and install all the required galvanized and PVC piping,fittings , flexible hose, wiring, cables, control panel for the system ,accessories,and all the requirements to complete the job perfectly and all the works must be according to instructions of ICRC engineer | ea | 2 |  | 0
| Total |  |  |  | 0
8 | Back up Generator
8.1 | Provision of materials and work rehabilitate and maintain the existing diesel generator ( Perkins 150 kVA), Work includes replace the fuel ,oil and air filters, replace the 130 A battery and all the requirements to complete the job perfectly and all the works must be according to instructions of ICRC engineer.Testing and successfully operating are included in the price. | ea | 1 |  | 0
8.2 | Provision of materials and work to rehabilitate fuel storage tank of (2000L) the work include pipes fittings ,valve ,level gauge with suitable oil paint after prime painting of anti-rust with all requirements to complete the job perfectly and all the works must be according to instructions of ICRC engineer | ea | 1 |  | 0
8.3 | Provision of material and work to Supply, install, connect and test new manual transferring switch of 250 Amps, to be fixed inside suitable box. Work includes all connections,cables and accessories and all requirements to make the job complete and according to the instructions of the ICRC Engineer. | ea | 1 |  | 0
8.4 | Provision of materials and work to make the job complete in every parts and details to supply and install (main control panel to serve both CUs), The main control panel should have a brand new insulated cabinet of (IP 55), main MCCB of (630 A) No.1, 100 A No.4, 75A No.4, and 10 A No.12 . phase failure and over under voltage protection device, The works includes all the necessary wiring, indication lamps, Ammeters, voltmeter with selector switch, terminals, cable glands and fixation, the required C.B, Bus bars, all requirements to make the job complete and according to the instructions of the ICRC Engineer.the price also include operating and Testing. | ea | 1 |  | 0
| Total |  |  |  | 0
9 | Civil Electro Mechanical and External Illumination work
9.1 | Provision of materials and work to construct an Operators Room of(3X4X3 m) 1) Excavating for foundation (60 width x 90 deep) cm & back-filling with clear and well compacted soil . 2) Providing materials and casting (1:2:4) reinforcement concrete for foundations in thickness of 30 cm over compacted 10cm layer of crushed stones. 3) Providing materials and building a wall of (40) cm thickness under DPC with solid concrete blocks (15x20x40) cm or stone & cement mortar (1:3) 4) Providing materials and building a wall of (20) cm thickness over DPC with concrete blocks (20x20x40) cm & cement mortar (1:3) 5) Providing materials and casting reinforced concrete for lintels, slabs, beams and columns using (1:2:4) ratio 6) Supply materials and plaster with cement mortar (1:3),the work includes emulsion paint with 2 layers 7) Providing materials and casting reinforced concrete by BRC for floor and aprons using (1:2:4) ratio . 8) Providing materials & installing (2.0x1.0) m. steel door made of metal sheet (1.25 mm thick), primer & two layers of oil paint and latch lock 1no. 9) Providing materials & installing (1.5x1.2) m. steel window including painting & glass. 10) Electrical works: The works include supplying, installing & testing all electrical installation. The material used in the installation should be brand new, using high tension plastic conduit in the electrical installation:- a. Supplying, installing & testing 20 A circuit breaker single phase brand new. Fixing & connecting the main power supply with all other requirements 1 no. b. Supplying, installing & testing fluorescent lamp 1x40 W using single core wire (2x1.5) mm2 inside plastic conduit with a suitable operating switch 2 no. and external light weatherproof outdoor economic bulb light complete with frame 2 no c-Supplying & installing switch plug 13 amp using (2x2.5) mm2 2 no. all the works must be according to instructions of ICRC engineer | Ls | 1 |  | 0
9.2 | Supply materials, tools and manpower to replace the damaged external fence (BRC )of (150 meter length Height of 1.8m ) the work include operate two BRC gates . technical details and selection of the colors as per the instructions of the ICRC Engineer | Ls | 1 |  | 0
9.3 | Provision of material and work to Chlorine Pit (6X3X2.4 m) 1-Excavating for foundation then compacting the section to minimum of 95% of Minimum Dry Density (MDD) 2-Casting (1:3:6) concrete for foundations in thickness of 10 cm over compacted 25cm layer of crushed stones . 3-Cast Reinforced concrete for base and the side walls and sloped wall using sulphate resistant cement and (1:2.4) mix ratio, the work includes works of the wooden frames, reinforcement, bitumen, and all accessories with all the required works to complete the Job. steel reinforcement 12mm , 2 layers (Top and Bottom) in both direction at 25cm c/c , the price include painting the surfces with 2 layers of bitumen paint , all the work should be according to the instructions of the ICRC Engineer. | Ls | 1 |  | 0
9.4 | Supply materials, tools, equipment and labor to construct overhead crane of capacity 0.5 ton, using 6" steel H section for columns, I section beam (8*4)" and bressing 2" angle iron very well fixing to the foot of column with the top face of wall or concrete pedestal, using 8mm thick plate (160*160)mm, M16 or anchor bolts, four for each column, well welding all the members connections joints, pulley, hook, stainless steel chain of suitable length, all steel faces should received two layers of anti rust and two layers of oil paints | Ls | 1 |  | 0
9.5 | Provision of material and work to supply and connecting and operating lighting pole diameter 4" height 5 m above the ground with the arm and all other necessary accessories to installing and connecting lighting fixture Ip 65 mercury type lamp 400 watt white color , internal wiring connection (2 * 2.5) mm with the work to pouring concrete foundation for the base of pole dimensions (40 cm x 40 cm * 1m) with a coating concert foundation using Asphalt paint with backfill and compaction , the price also include starters, switch boards and connecting them with power source , according to the technical specifications and under instruction of ICRC engineer. | ea | 6 |  | 0
9.6 | Provision of materials and work to rehabilitate the existed protection sunshade of the back up generator with external dimensions (5m X 5m, 3m height) , work include replace the damage corrugated galvanized steel sheets ,and painting the steel structure with one layer of anticorrosion paint then three layers of oil paint of good quality.and all the works must be according to instructions of ICRC engineer | M2 | 25 |  | 0
9.7 | Provision of materials and work to supply, manufacture and install Five protection sunshade of dimension(3.5m X 4.5m, 3m height) X4 (1 for HLP,1LLP Titin CU,1 for HLP,1LLP Thabatia ) and 1X(3m X 2m, 3m height) for chemical systems to be fixed on concrete base, using galvanized corrugated sheets gauge (22), (6nos.) of (5") steel square / circular pole, (2" x 4") oblong steel channel as beams over poles and steel section tube of (1.5" x 3") as purlines. Work includes; base plate, welding, screwing, roll bolts, , anti rust and oil painting, etc.) and all the works must be according to instructions of ICRC engineer | M2 | 69 |  | 0
| Total |  |  |  | 0
| Grand Total |  |  |  | 0
| Estimated duration | n° of calendar days