## BoQ
The International Committee of the Red Cross
WATER & HABITAT DEPARTMENT
Wajihia / CU / Rehabilitation
Wajihia/ Muqdadiya / Diyala Governorate
2017-05-07
Wajihia / CU / Rehabilitation
Wajihia/ Muqdadiya / Diyala Governorate
Item | Description | Unit | Qty | Unit Price (USD) | Total Price (USD)
1 | Suction system
1.1 | Provision of materials and work to supply and install a new foot valve (10") to the suction pipes, the work includes cutting, welding, painting and all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | ea. | 1 |  | 0
| Total |  |  |  | 0
2 | Low lift system
2.1 | Provision of material and work to make the job complete to Supply and Install brand new Low lift horizontal pump, western origin, end- section type, stainless steel shaft and BRONZE IMPELLER of specification (Q = 200 m3/h, H = 20 m, 22 kW), western type The work includes, dismantle the existing damaged pump, the modification of the suction and delivery pipes with all the accessories (anchor bolt, rubber washers, flanges, pressure gauges, connection cables, necessary pump alignment and fixation, testing and commissioning). The new LLP shall be connected to the existing control panel (starter will be fixed in control panal) with a proper length of cable , with and all the requirements to make the job complete and according to the instructions of the ICRC Engineer. Testing and successfully operating are included in the price. | ea. | 2 |  | 0
2.2 | Supply, install and operate new Butterfly valves of (10" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea. | 4 |  | 0
2.3 | Supply, install and operate new non return valves of (10" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea. | 4 |  | 0
2.4 | Supply, install and operate new Flexible Joint of (10" ) with all accessories , the works including all the rubber washers and all piping modification. | ea. | 2 |  | 0
| Total |  |  |  | 0
3 | High lift system
3.1 | Provision of material and work to make the job complete to Supply and Install brand new High lift horizontal pump, western origin, end- section type, stainless steel shaft and BRONZE IMPELLER of specification (Q=200m3/hr; H=40 m), motor (1500rpm, 50Hz, 380V), western type The work includes, dismantle the existing damaged pump, the modification of the suction and delivery pipes with all the accessories (anchor bolt, rubber washers, flanges, pressure gauges, connection cables, necessary pump alignment and fixation, testing and commissioning). The new HLP shall be connected to the existing control panel (starter will be fixed in control panal) with a proper length of cable , with and all the requirements to make the job complete and according to the instructions of the ICRC Engineer. Testing and successfully operating are included in the price. | ea. | 2 |  | 0
3.2 | Supply, install and operate new Butterfly valves of (10" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea. | 4 |  | 0
3.3 | Supply, install and operate new non return valves of (10" ) with all accessories of flange adapter, the works including all the rubber washers and all piping modification. | ea. | 4 |  | 0
3.4 | Supply, install and operate new Flexible Joint of (10" ) with all accessories , the works including all the rubber washers and all piping modification. | ea. | 2 |  | 0
| Total |  |  |  | 0
4 | Settling tanks
4.1 | Provision of material and work to repair and operate the whole settling tank ( 12m x 2.4m x 2.4m) after properly emptying them. The work includes completely washing and cleaning the walls and bottom using electric steel brush ( (grinding tool with steel brush) ) to clean rust area , removing all the accumulative sludge and heavy stacks of mud, cleaning and unclogging the sludge discharge pipes, repairing any defected parts in internal and external walls, bottom, V-notch, and repairing any leakage points, replacing of any defective valves and drainage valves, replace the damage and missing steel plates ,remove and re fix the reusable lamella sheets after proper cleaning, wash out , replacing the damaged bracing iron angle, painting with (2) layers of food grade epoxy paint for the internal walls and externally with suitable oil paint after prime painting of anti-rust in order to restore the tank as per its original design .with all requirements to complete the job perfectly and all the works must be according to instructions of ICRC engineer | ea. | 2 |  | 0
4.2 | Provision of material and work to maintain and repair the intermediate tank ( 6m x 2.4m x 2.4m ), The work includes completely washing and cleaning the walls and bottom, removing all the accumulative sludge , cleaning and unclogging the sludge discharge pipes,painting the interior surface with two layers of food grade epoxy paint and the externally with suitable oil paint after prime painting of anti-rust with all requirements to complete the job perfectly, also work includes repairing the leakages with all requirements to complete the job perfectly,all the works must be according to instructions of ICRC engineer | ea. | 1 |  | 0
4.3 | Provision of materials and work to supply and install flocculator mixer complete with steel shaft and propeller (motor of 0.75 kw). The work includes all the required material and tools to install,cable connection, electrical starter,Testing and successfully operating are included in the price. | ea. | 2 |  | 0
4.4 | Provision of materials and work to supply and install flash mixer complete with steel shaft and propeller (motor of 1.5 kw). The work includes all the required material and tools to install, cable connection, electrical starter,Testing and successfully operating are included in the price. | ea. | 2 |  | 0
| Total |  |  |  | 0
5 | Pressure filters
5.1 | Provision of material and work to maintain, repair and operate the horizontal pressure filters (cylinder shape dimeter of 2.4m x and length of 6 m ), the work includes , remove all the internal expired media ,repair the leakages, required welding of the nozzle base plate and fixed support, maintain and cleaning the filter (internally), coating the internal side with two layers of food grade epoxy and externally with suitable oil paint after the red oxide prim, supply and install nozzles , replace the defected or improper parts with new ones such as (washers, manometer gauge, bolts.), the work include all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | ea. | 3 |  | 0
5.2 | Provision of material and work to supply and laying filter media materials consists of different layers according to the Iraqi general DoW Standard. As below: 1-Coarse grade (9.5-13)mm , Height of 10 cm 2-Medium grade (6.5-9.5)mm , Height of 10 cm 3-Fine grade (2.5-6.5)mm , Height of 10 cm 4-Sand quartzes (0.6-0.65)mm , Height of 60 cm with laboratory tests certification , and all the requirements to make the job complete and according to the instructions of the ICRC Engineer. | m3 | 36 |  | 0
5.3 | Provision of materials and work to supply and install pressure relief valve . The work includes testing and operating. | ea. | 3 |  | 0
5.4 | Provision of materials and work to supply and install valve (3"). The work includes all required material and tools, testing and operating. | ea. | 3 |  | 0
5.5 | Provision of materials and work to supply and install valve (4"). The work includes all required material and tools, testing and operating. | ea. | 3 |  | 0
5.6 | Provision of materials and work to supply and install valve (6"). The work includes all required material and tools, testing and operating. | ea. | 3 |  | 0
5.7 | Provision of materials and work to supply and install, valve (8"). The work includes dismantling the existing damaged ones, testing and operating. | ea. | 9 |  | 0
5.8 | Provision of materials and work to supply and install Air Blower of capacity (11 - 14 kW). the work includes providing all ,check valves, vibration absorber base, safety valve, drain valve in lower point of pipes with air cleaner silencer on blower intake, works includes all mechanical connections with the filters, fittings, accessories, electrical connection as to instructions of ICRC engineer. | ea. | 2 |  | 0
| Total |  |  |  | 0
6 | Chlorination system.
6.1 | Provision of material and work to supply and install brand new Chlorinators of western origin (dosing equipment) wall mounted, of a capacity of (2Kg/h), ALLDOS type. The work includes the necessary fixation of the injector and the dosing device, supply, install and connect PVC pipe of 1" of a required length, all necessary fittings and strainer, non return valve. the work also includes the connection with the injection point on the discharge pipe in addition to the injection points of pre-chlorination in the settling tank with all required PVC piping and valves to control the dosing amount through both the pre-chlorination point and the delivery pipe, required frame and base, Testing and operating the chlorinators functionally and successfully. | ea. | 2 |  | 0
6.2 | Provision of material and work to supply, install and operate Chlorinator Boosting Pump (Q=5m3/h, H=60-80m) western origin, the work include the electrical starter (1.5KW), electrical connection, supply and connect galvanized pipe of 1" with all the necessary fittings | ea. | 2 |  | 0
| Total |  |  |  | 0
7 | Alum system.
7.1 | Provision of material and work torehabilitate the Alum tanks : PVC heat resistant solution preparation tank of (1000 L) the work include cleaning the tanks,all the fittings needed and PVC pipes 1`` to connect the system to the sedimentation tanks | ea. | 2 |  | 0
7.2 | Provision of materials and work to make the job complete in every parts and details to supply and install Alum mixer Power 0.5kw V= 3Ph , 380 Volt with speed gear box 1500rpm to 180rpm , 0.9 m length stainless steel shaft, and propeller The work includes supply and install all the required galvanized and PVC piping,fittings , flexible hose, wiring, cables, control panel for the system ,accessories,and all the requirements to complete the job perfectly and all the works must be according to instructions of ICRC engineer | ea. | 2 |  | 0
7.3 | Provision of materials and work to make the job complete in every parts and details to supply and install dosing pump : 224-230 L/h, H = 40m V = 3ph , 380Volt pressure 4 bar The work includes supply and install all the required galvanized and PVC piping,fittings , flexible hose, wiring, cables, control panel for the system ,accessories,and all the requirements to complete the job perfectly and all the works must be according to instructions of ICRC engineer | ea. | 2 |  | 0
| Total |  |  |  | 0
8 | elctro-mechanical work and Back up Generator
8.1 | Provision of material and work to supply, install, connect and operate brand new generator Perkins engine type of (250) kVA Prime, the work includes , transportation, loading, unloading to site, all required electrical connections, operational materials e.g. batteries, oil, filters, etc., with testing and operating, according to the technical specification. | ea | 1 |  | 0
8.2 | Provision of materials and work to rehabilitate fuel storage tank the work include pipes fittings ,valve ,level gauge with suitable oil paint after prime painting of anti-rust with all requirements to complete the job perfectly and all the works must be according to instructions of ICRC engineer | ea | 1 |  | 0
8.3 | Provision of material and work to Supply, install, connect and test new manual transferring switch of 400 Amps, to be fixed inside suitable box. Work includes all connections,cables and accessories and all requirements to make the job complete and according to the instructions of the ICRC Engineer. | ea | 1 |  | 0
8.4 | Provision of material and work to rehabilitate the cable tray, Work includes all requirements to make the job complete and according to the instructions of the ICRC Engineer | ML | 20 |  | 0
8.5 | Provision of materials and work to make the job complete in every parts and details to maintain and repair the main control panel, The work include replace ,the main MCCB of (630 A) No.1, replace the damaged protection and control device , phase failure and over under voltage protection device (Volts =380 V, Hz=50, adjustable voltage range 335-405 V),supply , install and connect a brand new starters with different capacities for LLP and HLP system ,The works includes all the necessary wiring, indication lamps, Ammeters, voltmeter with selector switch, terminals, cable glands and fixation, All the electrical provided materials, should be brand new and of western origin , with all the requirements to make the job complete and according to the instructions of the ICRC Engineer. Testing and successfully operating are included in the price. | ea. | 1 |  | 0
8.6 | Provision of material and work to maintain, repair , operate and paint the lighting poles, then supply and connect lighting lamps 400 watt white color , internal wiring connection (2 * 2.5) mm , starters, , switch boards and connecting them with power source ,accourding to the technical specifications and under instruction of ICRC engineer. | ea | 8 |  | 0
8.7 | Provision of materials and work to rehabiltate the tanker stand tap ( pipes 3") the work include all the fittings, valves with and all the requirements to make the job complete and according to the instructions of the ICRC Engineer | LS | 1 |  | 0
8.8 | Provision of materials and work to) rehabilitate and extend the protection shade for the CU of (25m X 5m, 3m height), work include replace the damage corrugated galvanized steel sheets ,and painting the steel structure with one layer of anticorrosion paint then three layers of oil paint of good quality. | M2 | 125 |  | 0
8.9 | Provision of materials and work to rehabilitate the existed protection sunshade for the back up generator with external dimensions of the back up generator (8m X 4m, 3m height) , work include replace the damage corrugated galvanized steel sheets ,and painting the steel structure with one layer of anticorrosion paint then three layers of oil paint of good quality. | M2 | 32 |  | 0
| Total |  |  |  | 0
| Grand Total |  |  |  | 0
| Estimated duration | n° of calendar days