## Technical Specifications
Item No. | Description | Unit | Quantity | Comment
Supply of Submersible pumps and cables
Item - 1 | Submersible Pump SP(8A -37 ) (European standard or equivalent) the impeller and the shaft should be made of stainless steel (work at water temp. arrive 50 deg.c ). (For borehole casing pipe Diameter 6''). Efficiency not less than 70% . Average (Head 180m Q=6 m3) Shaft materials :Stainless steel AISI 420 Impeller &sleeve Material: Stainless steel AISI 304 Pressure rating PN10 | pieces | 3
Item - 2 | Submersible Pump SP(17 -17 ) (European standard or equivalent) the impeller and the shaft should be made of stainless steel (work at water temp. arrive 50 deg.c ).(For borehole casing pipe Diameter 8''). Efficiency not less than 70% . Average (Head 170m Q=10 m3) Shaft materials :Stainless steel AISI 420 Impeller &sleeve Material: Stainless steel AISI 304 Pressure rating PN10 | pieces | 4
Item - 3 | Submersible Pump SP(30 -20 ) ( European made or equivalent) the impeller and the shaft should be made of stainless steel (work at water temp. arrive 50 deg.c ).(For borehole casing pipe Diameter 8''). Efficiency not less than 70% . Average (Head 200m Q=20 m3) Shaft materials :Stainless steel AISI 420 Impeller &sleeve Material: Stainless steel AISI 304 Pressure rating PN10 | pieces | 4
Item - 4 | Submersible Pump SP(30 -15 ) (European made or equivalent) the impeller and the shaft should be made of stainless steel (work at water temp. arrive 50 deg.c ).(For borehole casing pipe Diameter 8''). Efficiency not less than 70% . Average (Head 140m Q=20 m3) Shaft materials :Stainless steel AISI 420 Impeller &sleeve Material: Stainless steel AISI 304 Pressure rating PN10 | pieces | 5
Item - 5 | Submersible Pump SP(30 -10 ) (European made or equivalent ) the impeller and the shaft should be made of stainless steel (work at water temp. arrive 50 deg.c ). (For borehole casing pipe Diameter 8''). Efficiency not less than 70% . Average (Head 100m Q=20 m3) Shaft materials :Stainless steel AISI 420 Impeller &sleeve Material: Stainless steel AISI 304 Pressure rating PN10 | pieces | 4
Item - 6 | Submersible Pump SP(46 -15 ) (European standard or equivalent) the impeller and the shaft should be made of stainless steel (work at water temp. arrive 50 deg.c ).(For borehole casing pipe Diameter 8''). Efficiency not less than 70% . Average (Head 180m Q=22 m3) Shaft materials :Stainless steel AISI 420 Impeller &sleeve Material: Stainless steel AISI 304 Pressure rating PN10 | pieces | 4
Item - 7 | Submersible Pump SP(46 -10 ) (European standard or equivalent) the impeller and the shaft should be made of stainless steel (work at water temp. arrive 50 deg.c ). (For borehole casing pipe Diameter 8''). Efficiency not less than 70% . Average (Head 120m Q=30 m3) Shaft materials :Stainless steel AISI 420 Impeller &sleeve Material: Stainless steel AISI 304 Pressure rating PN10 | pieces | 4
Item - 8 | Supply of flexible power cable insulation from rubber , heavy duty, temp,rating (-25-60)C, wire from copper (3*6)mm. Type HO7RN-F Best quality. | m.l | 1500 | Each cable should not be less than 500 m
Item - 9 | Supply of flexible power cable insulation from rubber , heavy duty, temp,rating (-25-60)C, wire from copper (3*10)mm. Type HO7RN-F Best quality. | m.l | 1500 | Each cable should not be less than 500 m
Item - 10 | Supply of flexible power cable insulation from rubber , heavy duty, temp,rating (-25-60)C, wire from copper (3*16)mm. Type HO7RN-F Best quality. | m.l | 1500 | Each cable should not be less than 500 m
Supply of Submersible Motors and Control panel
Item - 11 | Submersible motor 7.5 KW (Riwindable ),(European standard or equivalent), bending wire copper made with socket and compound joint paste (work with temp. arrive 50 deg.C) (For borehole casing pipe Diameter 6'') . Output power: 7.5 kW Rated voltage :380V – 416V , Frequency: 50 Hz,three phase. Stainless steel AISI 304 including suitable cable joint | pieces | 6
Item - 12 | Submersible motor 11 KW (Riwindable ),(European standard or equivalent), bending wire copper made with socket and compound joint paste (work with temp. arrive 50 deg.C).(For borehole casing pipe Diameter 8'') Output power: 11 kW Rated voltage :380V – 416V, Frequency:50 Hz, three phase . Stainless steel AISI 304 including suitable cable joint | pieces | 20
Item - 13 | Submersible motor 15 KW (Riwindable ),(European standard or equivalent), bending wire copper made with socket and compound joint paste (work with temp. arrive 50 deg.C),(For borehole casing pipe Diameter 8'') . Output power: 15 kW Rated voltage :380V – 416V, Frequency:50 Hz, three phase. Stainless steel AISI 304 including suitable cable joint | pieces | 20
Item - 14 | Submersible motor 18.5 KW (Riwindable ),(European standard or equivalent), bending wire copper made with socket and compound joint paste (work with temp. arrive 50 deg.C).(For borehole casing pipe Diameter 8'') Output power: 18.5 kW Voltage: 400 V, Frequency:50 Hz, three phase. Stainless steel AISI 304 including suitable cable joint | pieces | 10
Item - 15 | Submersible motor 22 KW (Riwindable ),(European standard or equivalent), bending wire copper made with socket and compound joint paste (work with temp. arrive 50 deg.C).(For borehole casing pipe Diameter 8''). Output power: 22 kW Rated voltage :380V – 416V, Frequency: 50 Hz,three phase. Stainless steel AISI 304 including suitable cable joint | pieces | 10
Item - 16 | Submersible motor 30 KW (Riwindable ),(European standard or equivalent), bending wire copper made with socket and compound joint paste (work with temp. arrive 50 deg.C) (For borehole casing pipe Diameter 8''). Output power: 30 kW Rated voltage :380V – 416V,Frequency: 50 Hz,three phase. Stainless steel AISI 304 including suitable cable joint | pieces | 2
Item - 17 | Control Panel 7.5 kw Direct current. including(contectors.phasefailer.transformers.etc)(the component European made). Voltage: 400 V, Frequency:50 Hz, three phase including: main circuit breaker, main fuses, three phase-sequence-phase-loss relay, Overvoltage/Under voltage Relay (including high/low voltage cut off), Overload Relay including: Voltmeter and Amperemeter All internal equipment to IP2X standard protection level: minimum IP54 | pieces | 4
Item - 18 | Control Panel 11 kw type autotransformer including(contectors.phasefailer.transformers.etc)(the component European made). Voltage: 400 V, 50 Hz, three phase including: main circuit breaker, main fuses, three phase-sequence-phase-loss relay, Overvoltage/Under voltage Relay (including high/low voltage cut off), Overload Relay including: Voltmeter and Amperemeter All internal equipment to IP2X standard protection level: minimum IP54 | pieces | 5
Item - 19 | Control Panel 15 kw type autotransformer including(contectors.phasefailer.transformers.etc)(the component European made). Voltage: 400 V, 50 Hz, three phase including: main circuit breaker, main fuses, three phase-sequence-phase-loss relay, Overvoltage/Under voltage Relay (including high/low voltage cut off), Overload Relay including: Voltmeter and Amperemeter All internal equipment to IP2X standard protection level: minimum IP54 | pieces | 5
Item - 20 | Control Panel 18.5 kw type autotransformer including(contectors.phasefailer.transformers.etc)(the component European made). Voltage: 400 V, 50 Hz, three phase including: main circuit breaker, main fuses, three phase-sequence-phase-loss relay, Overvoltage/Under voltage Relay (including high/low voltage cut off), Overload Relay including: Voltmeter and Amperemeter All internal equipment to IP2X standard protection level: minimum IP54 | pieces | 5
Item - 21 | Control Panel 22 kw type autotransformer including(contectors.phasefailer.transformers.etc)(the component European made). Voltage: 400 V, 50 Hz, three phase including: main circuit breaker, main fuses, three phase-sequence-phase-loss relay, Overvoltage/Under voltage Relay (including high/low voltage cut off), Overload Relay including: Voltmeter and Amperemeter All internal equipment to IP2X standard protection level: minimum IP54 | pieces | 4
Item - 22 | Control Panel 30 kw type autotransformer including(contectors.phasefailer.transformers.etc)(the component European made). Voltage: 400 V, 50 Hz, three phase including: main circuit breaker, main fuses, three phase-sequence-phase-loss relay, Overvoltage/Under voltage Relay (including high/low voltage cut off), Overload Relay including: Voltmeter and Amperemeter All internal equipment to IP2X standard protection level: minimum IP54 | pieces | 2
B. Delivery
All Items should Be delivered to Water directorate warehouse /Iraq/ Duhok
C. Remarks And Condition
1 | Certification of origin for all offered items should be provided before delivery.
2 | Submit Manufacturer certification and test reports for all offered items should be provided before delivery.
3 | Catalogues (should be European Brand or equivalent Brand) and tech. specifications should be provided with offers .