## 150 kVa
ANNEX 1 - TECHNICAL SPECIFICATIONS FOR GENERATORS
TECHNICAL SPECIFICATIONS FOR 150 kVA GENERATOR
POS. | TECHNICAL SPECIFICATIONS | COMPARATIVE SPECIFICATION / REMARKS
Comparative specificatoin / remarks should indicate any deviation from technical parameter or functional description of tender specification or confirmation with "Yes" and if applicable further particularities.
1.0 | Diesel 50 Hz Generating Set, water cooled, incl. sound and weather proofed canopy; Stationary version, incl. lifting hook; tropicalized, ready for use, fitted as complete unit on a rigid base frame (e.g. skid mounted), consisting of Motor, Alternator, Battery, Fuel tank and separate switch board and accessories mentioned below. Norms and reference values to be followed: VDE, EN, DIN, ISO or equivalent norms. In particular VDE 0100 Teil 551/560, VDE 0108, DIN ISO 8528, DIN ISO 3046 and/or norms or other guidelines as may be menitoned in the present specification.
1.0.1 | Standby Power : min. 150 kVA (Tolerance + 10 / - 0 KVA), min. 120 KW Prime Power: min. 135 kVA (Tolerance + 10 / - 0 KVA), min. 108 KW taking into consideration the environmental conditions (Pos. 1.0.6) (Prime power - variable continuous output PRP per DIN ISO 8528, 24 h beyond variable output, overload 10% for 1 h within 12 hrs)
Please indicate:
1.0.2 | Variable continuous output PRP per DIN ISO 8528 by standard test conditions
1.0.3 | Variable continuous PRP per DIN ISO 8528 in reference to the environmental conditions (Pos. 1.0.6)
1.0.4 | Overall efficiency
1.0.5 | Type of Power Generator (Manufacturer, Brand, Model, Type)
1.0.6 | Site of operation / Purpose / Environmental conditions Outdoor installation in Iraq, up to +40°C, Altitude 300m NN, air humidity 60 %
1.0.7 | CE declaration of conformity by the manufacturer exists. Please attach the document to your offer.
1.0.8 | CE compliance of Generator, Motor and Alternator. Products/ Parts are labelled.
1.1 | Composition of unit
1.1.1 | Welded sectional steel base frame , warp resistant, lifting hook on each corner for easy lifting
1.2 | MOTOR, Norms and reference values: ISO 3046, DIN 6271, BS 5514
1.2.1 | Type: Diesel, direct injection, forced oil lubrication, fuel transfer pump
1.2.2 | Revs : 1500 rpm
1.2.3 | Speed regulation : Mechanical/Electronical
1.2.4 | Cooling: water cooled, considering a surrounding temperature of 40°C
1.2.5 | Alternator, battery charging: Integrated 12/24V
1.2.6 | Starter motor: integrated 12/24V
1.2.7 | Starter battery fitted to the aggregate incl. hood, 12/24V, dry pre-charged
1.2.8 | Fuel tank: steel, fitted to the frame, incl. fuel level gauge. Tank capacity: at least for a 8 hours run under maximum continuous output.
Please indicate:
1.2.9 | Motor (engine) brand and designation, Model and Type
1.2.10 | Number of cylinders and cubic capacity
1.2.11 | Fuel tank capacity
1.2.12 | Oil capacity
1.2.13 | Motor capacity as per ISO 3046-7 based on 25°C intake temperature, 25°C cooling water intake temperature, 1.000 mbar air pressure, 30% air humidity – (KW)
1.2.14 | Motor capacity as per ISO 3046 in reference of the environmental conditions, mechanical (KWm)
1.2.15 | Motor capacity as per ISO 3046 in reference to the environmental conditions, electrical (KWe)
1.2.16 | Motor efficiency
1.2.17 | Fuel consumption as per ISO 3046-1 including attached pumps. Lower fuel heating value42.700 KJ/kg Tolerance + 5% at PRP 100% load in g/KWh
1.2.18 | Diesel consumption at 75% load
1.2.19 | Diesel consumption at 50% load
1.2.20 | Lubrication oil consumption (ltr/h) under standard conditions
1.3 | ALTERNATOR Norms and reference values: VDE 0530, BS 4999, UTE NFnC 51.111, IEC 34.1, NEMA MG 21
1.3.1 | Three-phase current alternator as per VDE 0530, internal pol machine with damping winding, self-regulating, self-starting
1.3.2 | Voltage rigidity : max 5 %
1.3.3 | Nominal voltage: 230V alternating current, 400V three-phase current
1.3.4 | Frequency: 50 Hz, and No of Poles =4
1.3.5 | Power factor: cos phi 0,8
1.3.6 | Insulation class: H, and No of Bearings = single
1.3.7 | Isolation good for tropic climate, Connection Type = STAR
1.3.8 | Radio interference suppression according to VDE 0875 “N”
1.3.9 | Protection class DIN 40050, IP 23
1.3.10 | G3 Classification according to DIN ISO 8528
1.3.11 | Electronic type automatic voltage regulator (AVR)
Please indicate:
1.3.12 | Alternator brand, model, type
1.3.13 | Efficiency factor of Alternator
1.4 | Exhaust System, Soundproofing
1.4.1 | Weather and sound proofed canopy incl. exhaust silencer. High corrosion resistance: stainless covered with zinc and made in dichromate. Large doors allow easy access to the generator set for service and monitoring purposes. Lockable doors with one window showing the control panel, fully assembled for immediate use. Exhaust system fully integrated (inner mounted).Sound protection LWA below 89 dB (A)pW. Emergency stop button is accessible from outside enclosure.
Please indicate:
1.4.2 | Acoustic power (LWA) [dB (A)]
1.4.3 | Acoustic pressure level at 1 m distance
1.4.4 | Acoustic pressure level at 7 m distance
1.4.5 | Acoustic pressure level at 10 m distance
1.5 | Control fittings / Measuring Instruments / Switch board
1.5.1 | Tap changer with connection to the exist steel board in the site
1.5.2 | Motor protection accessories (Oil pressure, water temperature, excessive revs) Generator protection switch, thermic-magnetic overload protection, protection of Instruments and indicators
1.5.3 | Battery-charging control light, oil-pressure warning light, excessive-temperature warning light, light test, excessive revs alarm, false start light, emergency-off light, central warning light
1.5.4 | Measuring instruments, switches; 1 x Ampere meter, 1 x Voltmeter with switch, 1 x frequency measuring unit, 1 x operation hours counter, emergency “off” button, manual mode switch
1.5.5 | Labeling of all components in English language
Please indicate:
1.5.12 | Dimensions of one unit: (length x width x height)
1.5.13 | Weight of one unit in kg (without any fillings)
1.6 | DOCUMENTATION
1.6.1 | Manual for installation, commissioning and use plus a spare parts catalogue for each part of the generator (motor, generator, switch board, wiring diagram) in English and if available Arabic language
1.7 | LOCAL AGENCY / AFTER SALES SERVICE
Please indicate:
1.7.1 | Address of the local agency or agency within the region
1.8 | Spare parts / Maintenance parts / Consumables covering 1.000 hrs of operation
1.8.1 | 6 pc. Oil filters
1.8.2 | 2 pc. Air filter
1.8.3 | 6 pc. Fuel filter ext.
1.8.4 | 1 set of seals, screws, nuts, etc, for 1.000 hrs of operation
1.8.5 | 1 set of V-belt
1.8.6 | 1,500 liters of diesel to the exist tank in the site
1.9 | Standard tool set
1.9.1 | Standard tool set to provide maintenance and small repairs up to 1.000 hrs of Operation
Please indicate:
1.9.2 | Tool set list as per 1.9.1
1.10 | Dimensions / Weights
1.10.1 | Dimensions (length x width x height) without canopy
1.10.2 | Dimensions (length x width x height) incl. canopy
1.10.3 | Weight (kg) empty without canopy
1.10.4 | Weight (kg) empty incl. canopy
1.11 | Insurance / Conditions
1.11.1 | The cost of transit insurance relating to the items to be transported by the contractor to the site of work shall be borne by the contractor/supplier and the quoted price shall be inclusive of this cost.
1.11.2 | The offered equipment shall be brand new with state of art technology and proven field track record. No prototype equipment shall be offered.
1.12 | Installation, connection and Transportation
1.12.1 | The Installation on site with the required accessories are included in the price.
1.12.2 | cable size 4*90mm (25-30 meters) to connect with exist board
1.12.3 | Wire 2.5 *4 mm for control (25-30 meters) to connect with exist board
1.12.4 | cable tray 30 meteres
1.12 | Canopy Features
■ Compatible with 2000/14/EC directives, certified noise emission level, ■ 2 or 4 points transport possibility according to cabin size, ■ Hidden exhaust inside the canopy, ■ Emergency stop button located on the canopy, ■ Improved air suction channel to ensure homogenous cooling in the canopy, ■ Radiator air outlet and exhaust with designed towards above, ■ Lid on cab that provides to be filled up water and antifreeze easily to the radiator, ■ Amplified paint system against corrosion and rust, ■ Improved performance in terms of sound insulation, ■ Demounted parts that make transportation and maintenance easier,