## BoQ
Form D 4.2.4 Price Schedule 2 – Construction Build Works for the site
Bill of Quantity BoQ)
Reconstruction of SAMSIEH SUB Primary Health Care Center in Anna, Anbar, SAMSIEH City
Procurement Reference No: ASB 1903/WORKS/2020/0001/2
Note: Please fill out the numbers in the BoQ in english written numbers, otherwise the financial proposal will be disqualified.
# | Item | Unit | Quantity | Price $ | Total $
A : Site Preparation Works
1 | Site preparation: | M2 | 900 |  | 0
Supply materials, tools, heavy construction equipment and manpower to demolish and remove all concrete structure, walls, blocks and foundations which existing up and down the ground level and 25cm of the existing soil of project ground. All project area shall be cleared of grass and weeds to at least a depth of 30 cm. Cleared of structures, pavement, sidewalks, concrete or masonry debris, trees, logs, upturned stumps, loose boulders, and any other objectionable material of any kind which would interfere with the performance or completion of the work, create a hazard to safety, or impair the subsequent usefulness of the work, or obstruct its operation. The price should include withdrawal of surface, ground water and ponds within the area of the project (if any). In addition to remove trees and other natural vegetation outside and inside the actual lines of project area, and all debris from the site to a dump site approved by the relevant authority. leveling and compacting all the project area (after removal of 25 cm of the existing project soil) using heavy construction equipment - single drum sheep feet and vibratory road roller compactor, the natural ground compaction of the project should not be less than 90% of MDD to comply with the modified proctor test and marking and planning the buildings of the project. The work includes delivering all existing materials and furniture inside the project before demolishing the buildings to End User warehouses and delivering them by official storage documents according to instruction of the supervisory committee, cleaning and washing all parts of the project after completing the construction works. All needed work to complete the job will be included within the price.
| Excavation Works:فقط للمواقع التي تحتاج | M3
Excavation in all types of soil (even rock layers, existing asphalt, concrete foundations, etc..) for the project area starting at the existing ground level down to the required depth approved by the engineering committee, removal of all material to a site approved by local authorities. The price include cleaning and leveling the bed of the excavation, compaction using heavy construction equipment - single drum sheep feet and vibratory road roller compactor (the compaction of these areas should not be less than 90% of MDD to comply with the modified proctor test) and withdrawing the underground water if the groundwater level is high on a daily basis using water tank truck until the completion of the foundations and all the required works to complete the Job. All needed work to complete the job will be included within the price.
2 | Spreading Stone Layer: فقط للمواقع التي تحتاج | M2 |  |  | 0
Supply materials, tools and manpower to spread and pave stone layer of class B regularly under the buildings areas, the stone layer thickness not less than 30 cm, the work includes excavating drainage channel to withdrawal the underground water if the groundwater level is high on a daily basis using water tank truck, compaction of the stone layer well using vibratory road roller compactor and all the required works to complete the Job.
3 | Spreading Sub-base Layers | M3 | 510 |  | 0
Supply of materials, tools and manpower for filling (in layers not exceeding 25cm, including compaction up to 95% of MDD to comply with the modified proctor test ) with sub base (type B) up to the required levels for the area of project, with required treatment. All needed work to complete the job will be included within the price.
B: Civil Works
B-1: Concrete Works
4 | Laying One Layer of Thick Nylon | M2 | 150 |  | 0
Supply materials, tools and manpower for laying one layer of thick agricultural nylon of 1mm thick. The nylon should lay before casting the concrete covering , with all the required works to complete the Job.
5 | Sulphate Resistant Plain Concrete
Supply materials, tools and manpower to cast Sulphate resistant plain concrete with compressive strength 21 MPa , (Slump 5"), the work includes expansion joints every 20 m2 and according to the instructions of engineering committee, and all the required works to complete the Job.as the following:
A | Minimum 10 cm thick Under foundations (Blinding) | M2 | 140 |  | 0
B | Minimum 15 cm thick and 25cm width with using Sika proof for D.P.C layer using heavy thickness steel frame of 15 cm height | M.l | 215 |  | 0
C | Minimum 10 cm thick under marble tiles. | M2 | 360 |  | 0
6 | Reinforced Concrete
Supply materials, tools and manpower to cast reinforced concrete with compressive strength 26 Mpa for all concrete works , the work includes shuttering( formwork), reinforcement and all accessories as per the attached drawings and technical specification, the price should include using high yield strength of (420N/mm2) deformed steel reinforcement (Ukraine or Turkish origin which is available in the markets and conform to the required specifications), coating the buried foundations and any part of columns using the tar class II or III and emphasis on water spraying (Curing) not less than 7 days, the use of Jute Cloth in the curing process with all the required works to complete the Job, as following:
A | Foundations using sulfur resistant cement | M3 | 69 |  | 0
B | Roofs of 18 cm thick and parapets | M3 | 78 |  | 0
C | Columns | M3 | 1 |  | 0
D | Drop beams (The prominent part of the ceiling is calculated) and | M3 | 5 |  | 0
E | lintel beams above the openings of doors and windows | M3 | 6 |  | 0
F | Steps, landings and flights (sulfur resistant cement is used for the part down D.P.C Layer). | M3 | 5 |  | 0
B-2: Building Works With bricks
7 | Build The Walls Under D.P.C Layer | M3 | 43 |  | 0
Supply materials, tools and manpower to build the walls under D.P.C layer using red clay bricks type A of (24x 12x 7.5) cm and cement-sand mortar (1:3) as per the attached drawings, the required brand is ASO or Al-Hilal , the work includes filling joints and spaces by sulfur resistant cement-sand mortar (1:3) , plastering the walls with cement –sand mortar (1:3) and spreading for both sides of the walls with tar Class II or III with all the required works to complete the Job.
8 | Build The Walls Above D.P.C Layer | M3 | 183 |  | 0
Supply materials, tools and manpower to build the walls building and parapets walls of 24cm thick above D.P.C layer and 12 cm thick for the partitions using red clay bricks type A of (24x 12x 7.5) cm and cement-sand mortar (1:3) as per attached drawings, the required brand is ASO or Al-Hilal with all the required works to complete the Job.
B-3: Backfilling With River Sand Layers
9 | Backfilling Works: | M3 | 370 |  | 0
Supply of materials, tools and manpower for filling in layers not exceeding 40cm thick for the one layer, including good compaction using approved river sand up to D.P.C layer level inside the building and in any area required within inside the building with all necessary works, with required treatment. All needed work to complete the job will be included within the price.
B-4: Tiling and False Ceiling Works
10 | Marble Tiles for The Building Floors and Entrance | M2 | 285 |  | 0
Supply materials, tools and manpower to finish the buildings floors and building entrance using marble tiles of (30X60) cm dimensions and 2 cm thick from a first-class of Turkish origin (original, not commercial or imitative) and cement sand mortar (1:3) , the tiles final faces should be flat and free from any ripples, the price includes steps of polishing and glazing the marble tiles in site and not limited to fill the joints with white cement, use of pieces and strips of marble tiles (Different in terms of colors) to work decorations and geometric shapes in the floors according to the direction of the Engineering Committee, cleaning the concrete floors well before finishing the floor using the tiles and taking into consideration the make of joints which not exceeding the width it of 1.5 cm for each 8 to 12 M.l and it is subsequently filled with Sikaflex construction AP with Back up rod for joints tiles . The contractor must submit samples to the Engineering Committee for the approval of one of the sample and which must be subject to the full physical and chemical laboratory tests and according to Iraqi standard specifications, with all the required works to complete the work.
11 | Ceramic Tiles
Supply materials, tools and manpower to finish the walls of sanitary units, kitchen, and 1.2 m height skirting for all the building walls and floors of the sanitary units and kitchen using ceramic tiles from a first-class and cement sand mortar (on two-layer of plastering of cement mortar (1: 2) and (1:3)), the tiles final faces should be flat and free from any ripples, solution of water and bonding agent. The contractor must submit samples to the Engineering Committee for the approval of one of the sample and which must be subject to the laboratory tests and according to Iraqi standard specifications, installation of aluminum ceramic corner tile trim at the corners and edges of the walls, with all the materials needed to install, filling the joints with white cement and polishing, with all the required works to complete the work.
A | Ceramic tiles for the walls of (30x60) cm dimensions | M2 | 440 |  | 0
B | Ceramic tiles anti slip for the floors of (30x30) cm dimensions | M2 | 40 |  | 0
12 | Roofing Using Concrete Tiles | M2 | 357 |  | 0
Supply materials, tools and manpower for roofing works according to the technical specifications, the work includes the following:
A: Cleaning the roof well using air compressor and coating all the roof with two layers of liquid bitumen primer for waterproofing (flancote).
B: Spreading opposite layers of tar of (30/20) grade and laying between them a good quality of SBS modified bitumen waterproofing membrane (Saudi or Jordanian origin) of 3mm thick, the tar layers and bitumen waterproofing membranes level must be raised 20 cm height around water baffles for the building and overlapping between the bitumen waterproofing membrane pieces not less than 15 cm for both directions.
C: Spreading high density and compressed corks layer of 5 cm thickness and laying one layer of thick agricultural nylon (polyphone sheets 1 mm).
D: Spreading clean river sand layer with 8 cm thickness at the lowest area and increase the thickness according to the required slope.
E: Finishing with concrete tiles of (80x80x4) cm thickness, taking into consideration the slope towards water drainage.
F: Casting the edges by plain concrete of 21 Mpa compressive strength.
G: Filling the joints with bitumen mastic with cautery
with all required works to complete the job.
13 | Perforated Gypsum Board False Ceiling Tiles : | M2 | 290 |  | 0
Supply and install perforated gypsum board false ceiling tiles of 60x60 cm dimension and 10 mm thickness which should be installed on the 3.0 m height from the ground level of the building, the work includes provision and installation of heavy thickness metal structure for false ceiling( L, T sections, hold down clips), galvanized steel rod 5mm (1.2x1.2m) for fixing it with the ceiling by screws "butterfly" type, and all installation and connection accessories with all works to complete the job.
14 | PVC False Ceiling : | M2 | 35 |  | 0
Supply and install PVC false ceiling tiles of 60x60 cm dimension and 10mm thick which should be installed on the 3.0m height from ground level of the building for the sanitary units and kitchen, the work includes provision and installation of heavy thickness metal structure for false ceiling( L, T sections, hold down clips), galvanized steel rod 5mm (1.2x1.2m) for fixing it with the ceiling by screws "butterfly" type, and all installation and connection accessories with all works to complete the job.
B-5: Plastering, Exterior Cladding for The Building and Painting Works: Including all materials, scaffolds, workmanship, tools and anywhere else needed
15 | Smoothed Cement Plastering: | M2 | 620 |  | 0
Supply materials, tools and manpower to plaster the building external walls and some parts of the front entrance of the building as per shown in attached drawings using smooth-finished cement plastering of 20mm thick with cement sand mortar (1:3) using aluminum straight edges, plastering in two coats over, the work includes spreading one layer of cement splash dash, putting a layer of metal mesh on the area under the cement plastering which should be installed at the linking area of the concrete beams and columns with the bricks walls with decoration works in the plastering according to supervisory committee directions, and all the required works to complete the work.
16 | Gypsum Plastering | M2 | 510 |  | 0
Supply of materials, tools and manpower for gypsum plastering of the two layers minimum 20mm of brown and white gypsum using aluminum straight edges for the interior walls up to the concrete ceiling, the price includes one layer of cement splash dash under Gypsum plastering with cement-sand mortar, putting a layer of metal mesh on the area under the gypsum plastering which should be installed between the linking area of concrete beams and columns with the bricks walls and all the required works to complete the work.
17 | Plastic Painting for Internal Walls: | M2 | 510 |  | 0
Supply of materials, tools and manpower to paint the interior walls with 3 layers of plastic painting (Jotun, Betek, CAPAROL, Polisan, dyo). The job includes cleaning the walls and ceilings, removing the dirt and dust. All needed works to complete the job, shall be included within the price.
18 | Plastic Painting For External Walls: | M2 | 600 |  | 0
Supply of materials, tools and manpower to paint the exterior walls and ceiling, with three layers of plastic (silicon water proof) paint (Jotun- Jotashield, Betek, CAPAROL, Polisan, dyo). The job includes cleaning the walls, removing the dirt and dust. All needed works to complete the job, shall be included within the price.
19 | Cladding External Walls of The Building Facade
Supply materials, tools and manpower for cladding the external walls for the facade of the building with limestone panels type (Mosul - Ba'adhira) and and first-class marble tiles of Turkish origin (approved sample) using mechanical method for the installation and using reinforcement steel layer (BRC) of (6 mm) diameter to install stone panels and marble tiles on the walls, price should include filling the spaces between the stone and marble tiles and the walls by using cement mortar (1:3) and the joints between stone with white cement and crushed stone powder (1:1), using solid copper wire for the installation of stone, installation of the stones panel on the walls and above the openings of doors and windows and sunshades using steel angle section of 2 inch and 3 mm thick and polishing stone very well taking into account the special safety requirements, and according to the technical specifications and attached drawings as follows (The contractor should be complied with all forms and types of stone and all other details referred to in the attached drawings and designs),and all the required works to complete the work. As following:
A | Stones panels with thickness of not less than 5 cm | M2 | 22 |  | 0
B | Stones Frame of 20 cm height ( Coplan- كوبلن صدر طير) | M.l | 20 |  | 0
C | Stones Frame of 20 cm height and 5 cm thick ( Coplan) | M.l | 20 |  | 0
D | Stones Frame of 15 cm height and 5 cm thick ( Coplan), which it is also used around all windows of a building. | M.l | 126 |  | 0
E | Marble tiles of 2 cm thick | M2 | 26 |  | 0
B-6: Doors, Windows, Handrails and Sun Shed works
20 | Teak (Saj) Wooden Doors: | Ea. | 13 |  | 0
Supply and install D1 teak (saj) leave wooden doors of 2.25x1 m dimensions with 6x3 inch red cedar (jawi) frame of 2.35x1.1 m dimensions (from outside to abroad) as per the attached drawings. Price of the work shall include the thickness of teak layer not less than 5 mm thick for each door face, installing geometric motifs on the exterior and interior faces for the door made of Jawi wood, Jawi wood frame around the door of 5 cm width and 1 cm thick, heavy duty door locks and handles from Italian or Turkish origin - first class, heavy duty Stainless Steel door hinges of 5 screws, fixing a stopper on the floor or wall, installing aluminum sheet of 25 cm height and 2 mm thick in the door end and from both the directions, painting the door and frame with three layer of liquid teak paints, with all the required works to complete the work. As following:
21 | Steel Doors:
Supply and install double face steel door, the partitions inside the door included every 20cm by steel Square hollow section (4cmX4cmx2mm), and covered with steel plate 1.5 mm thickness on both sides with the use of geometric engravings on the steel plates designed by CNC machines using steel plate 2 mm thick for the doors mentioned in attached drawings, the frame shall be from steel C section of 3 inch and 3 mm thickness and steel angle section of 1 inch and 2 mm thickness ( double steel frame), the work including all necessary fixings hinges, doors handles, locks with key from Italian or Turkish origin - first class, hands locks and fixing a stopper on the floor or wall, glazing using stained glass of 6 mm thick , insulation foam, accessories, mastic, hardware and painting with anti-rust paint and 3 layers of oil paints type hammer finish, locks, connections accessories, as per attached drawings, and all the required works to complete the work. As following:
A | D3 Steel door of 2.75 x 2.75 m dimensions (two leaves door) | Ea. | 1 |  | 0
B | D4 Steel door of 2.75 x 1.4 m dimensions (two leaves door) | Ea. | 1 |  | 0
C | D6 Steel door D6 of 3.00 x 2.1 m dimensions (two leaves door) | Ea. | 1 |  | 0
22 | PVC Door: | Ea. | 4 |  | 0
Supply and install PVC door with frame(D5) of 2.2 x 0.9 m dimensions (the door color should be dark brown) for sanitary unit, It is installed in the walls by frame of steel C Section of 3 inch dimension, 3mm thick and painting with three layers of oil based paints in addition to anti rust primer. The PVC sections and panel lambrins should be wide section and from Turkish origin - first class as per the attached drawings with all accessories and installation of heavy duty locks, hinges and handles from Turkish origin, with all the required works and accessories to complete the Job.
23 | Steel Sliding Door For The Main Entrance and Parking | Ea. | 1 |  | 0
Supply and install steel sliding door of (D7) 3.25x 2.1 m dimensions , the partitions inside the door included every 20cm by Square hollow section (4cmX4cmx2mm), the frame door ( the moving part ) from Square hollow section of 3 inch and 3 mm thick, and covered with steel plate 1.5mm thickness on back side with the use of steel plates of 2 mm thick designed by CNC machines from the front side, the main frame shall be from steel C section of 4 inch and 3 mm thickness and steel angle section of 4 inch and 3 mm thickness ( double steel frame) and the door's rail of A channel of 3 inch and 4 mm thick and mild steel round bar of 12mm diameter which should be installed by reinforced concrete base , the work including all necessary fixings hinges, doors handles, locks with key from Italian or Turkish origin - first class and fixing a stopper on the floor or wall, insulation foam, accessories, mastic, hardware, and painting with anti-rust paint and 3 layers of oil paints type hammer finish, locks, connections accessories, as per attached drawings, with all the required works to complete the work.
24 | Aluminum Window
Supply and install aluminum window with it is frame and installing by frame of steel C Section of 3 inch, 3mm thick and painting with three layers of oil based paints in addition to anti rust primer. Price of the work shall include using heavy thickness not less than 1.3mm and 7.5 cm width aluminum sections of Turkish origin - first class as per the drawings, installation of heavy duty locks and handles, installation of tinted glass of 6 mm thick, anti-insect netting mesh, steel guard frame (Steel Burglar frame) as per attached designs (The contractor should be complied with all details and design of steel guard frame referred to in the attached drawings) with painting the steel frame and guard frame with 3 layer of oil based paints “type hammer finish” in addition to anti rust prime coat, all the required works and accessories to complete the Job. The doors dimensions as followings:
A | W1 Aluminum window of 1.6 x 1.8 m dimension | Ea. | 13 |  | 0
B | W2 Aluminum window of 0.5x 0.75 m dimension | Ea. | 4 |  | 0
C | W3 Aluminum window of 1.4 x 0.8 m dimension | Ea. | 3 |  | 0
D | W4 Aluminum window of 1.2 x 1.4 m dimension | Ea. | 1 |  | 0
25 | Roller Curtains
Supply and install roller curtains (Zebra Curtains) of high thickness for windows, it should be of good quality of Turkish and approved by engineering committee. For more details please see compliance sheet. The curtains dimensions as followings:
A | Roller Curtains of 1.7 x 1.9 m dimension | Ea. | 13 |  | 0
B | Roller Curtains of 1.4 x 1.9 m dimension | Ea. | 4 |  | 0
26 | Steel Handrail: | M.l | 14 |  | 0
Supply of materials, tools and manpower to install steel handrail of 90cm height for external stairs using steel tubes and sections as per attached the drawings. The price includes painting with 3 layer of oil based paints “type hammer finish” in addition to anti rust prime coat. All needed work to complete the job will be included within the price.
27 | K- span Sun Shed works : | M2 | 50 |  | 0
Supply of materials, tools and manpower to install K- span sun shed which should be installed in the main front entrance for the project. The price includes:
A- Excavation for the columns footing (60x60x60cm).
B- Providing and installing (4) anchor bolts of Ø16mm and length of (40cm) for each column.
C- Providing and installing base plate of (200x200x10mm) for each column.
D- Casting column footing (60x60x60cm) using (C21MPa) concrete and sulphate resistance cement for each columns.
E- Providing and installing columns of Steel hollow square section of 100x100x3mm with height 3 m, the distance between columns shall not exceed 3 m
F-Providing and installing steel drain trench using steel plate of 2 mm
G-Providing and installing K- span sunshade, using plate of 0.8 mm thick,.
H-Painting the steel structure with one layer of anti rust and three layers of oil paint.
All needed work to complete the job will be included within the price.
B-7: Billboard, Room Title Board and Portable Fire Extinguisher
28 | Aluminum Composite letters | M2 | 6 |  | 0
Supply and install the PHCC name in the building facade in the form of composite letters that should be cut by CNC cutting machine by using aluminum panels with the panels thickness not less than 5 mm and its bases from PVC panels of 1 cm thick as per the colors determined by the engineering committee. The letters structure should be flat surfaces and free of metal impurities and should be installed on the wall using silicone adhesive glue and plastic fisher screw wall plug, with all the required works to complete the Job.
29 | Room Title Boards: | Ea. | 14 |  | 0
Supply and install room title name made of thick plastic sheet of 15x35 cm dimensions, the price should include printing the required titles on it, using plastic fisher screw wall plug to fix it in the walls. All needed work to complete the job will be included within the price.
30 | Portable Fire Extinguisher Powder | Ea. | 7 |  | 0
Supply and install portable fire extinguisher powder of 12 Kg capacity-(A.B.C) type which should be installed in the locations determined by supervisory committee. The installation shall be complete with brackets and it should be usable for at least three years from the date of receipt all in accordance with the Civil Defense specification, with training candidates from the end user on how to use them.
B-8: Passageway and The External Corridors Works
31 | Supply materials, tools and manpower to cast the new passageways around the building and the external corridors which lead to the building of 1.5 m width according to the follow items:
A | Spreading thick agricultural nylon layer- polyphone sheets of 1 mm thick before casting concrete ( under foundation and passageway floor) | M2 | 40 |  | 0
B | Casting Sulphate resistant plain concrete of 20 cm thickness and 30 cm width for passageway foundation with compressive strength 21 MPa, (Slump 5”) , all the required works to complete the Job | M3 | 8 |  | 0
C | Build the passageway walls using red clay bricks type A of (24x 12x 7.5) cm and cement-sand mortar (1:3), the required brand is ASO or Al-Hilal with height 80 cm and 24 cm width, the work includes smoothed plastering for the external and internal wall with cement-sand (1:3) and spreading the internal wall with tar Class II or III. | M3 | 26 |  | 0
D | Spreading well compacted river sand layer with thickness not more than 40 cm for each layer under passageways floor. river sand layers shall be watered, leveled and compacted well. With required treatment | M3 | 185 |  | 0
E | Casting smooth Sulphate resistant plain concrete for passageway floor with compressive strength 21 MPa, (Slump 5”) and 10 cm thickness, the work includes expansion joints every 20 m2 and it is subsequently filled with Sikaflex construction AP with Back up rod, and all the required works to complete the Job. | M2 | 170 |  | 0
F | Finishing the front, side walkways and entrance to the buildings floors using Polished cement mosaic tiles (approved samples by supervisory committee) of (40X40) cm dimensions best quality and cement sand mortar (1:3) , the tiles final faces should be flat and free from any ripples, the price includes steps of polishing and glazing the mosaic tiles in site and not limited to fill the joints with white cement, the work includes casting sulphate resistant plain concrete with compressive strength 21 MPa , (Slump 5") under mosaic tiles with all required work to complete the job. | M2 | 100 |  | 0
G | Painting the Brick walls from outside with three layers of plastic (silicon waterproof) paint (Jotun, Betek, CAPAROL, Polisan, dyo) | M2 | 150 |  | 0
B-9: Parking Works
32 | Parking of the Project | M2 | 120 |  | 0
: Supply materials, tools and manpower to cast the parking, the work includes leveling the ground, compaction of existing ground (which should not be less than 90% of MDD to comply with the modified proctor test), filling in layers not exceeding 25cm, including compaction up to 95% of MDD to comply with the modified proctor test with sub base (type B)up to the required levels (the required levels of the parking floors is 40 cm under the passageway concrete floor ) and according to the supervisory committee directions, the price should include spreading thick nylon layer of 1 mm thick and casting with compressive strength 21 Mpa reinforcement sulphate resistance concrete with BRC layer of 6 mm thick, smooth surface and 15 cm thick using Helicopter for leveling concrete surface, working expansion joints every 20 m2and subsequently filled with bitumen mastic with cautery, and all the required works to complete the Job.
33 | Metal Sunshade Works | M2 | 60 |  | 0
supply materials, tools and manpower to install metal sunshade roof of 3m height which should be installed in the parking, according to details below:
A- Steel square column of 3x3 inch and 4 mm thick and the distance from column and another should not be more than 3 m.
B- Base plate of 25x25 cm dimension10 mm thick to install the sunshade steel structure with floors using rot bolts of 18 mm diameter with all required works
C- Steel hollow square section for beams of roof structure of 3x3 inch dimensions and 4 mm thick.
D- Steel hollow rectangular section for sub beam 1.5x3 inch and 3 mm thick.
E- 0.8mm thick corrugated plates for the roof, fixed by screws and overlapped in order to prevent water leakage.
The work includes all cutting and welding works, painting with anti-rust and three layers of oil paint for all steel structure with all the required works to complete the Job.
B-10: Fence Wall Works
34 | Laying one Layer of Thick Nylon | M2 | 60 |  | 0
Supply materials, tools and manpower to spread thick agricultural nylon layer (polyphone sheets 1 mm thick) over the sub base layer
35 | Sulphate Resistant Plain Concrete for Blinding | M2 | 60 |  | 0
Supply materials, tools and manpower to cast the Blinding of 10 cm thick and 21Mpa compressive strength, with all the required works to complete the Job.
36 | Reinforced Concrete for Foundation | M3 | 18 |  | 0
Supply materials, tools and manpower to cast 26 MPa sulphate resistance reinforced concrete of (30x50) cm the price should include, high yield (420N/mm2) deformed steel reinforcement (Ukraine or Turkish origin which is available in the markets and conform to the required specifications), timber formwork and shuttering. For more details, please see attached drawings.
37 | Reinforced Concrete for The Columns | M3 | 9 |  | 0
Supply materials, tools and manpower to cast reinforced concrete for the columns of (30x40) cm dimensions, 2m height above the D.P.C and 26 MPA compressive strength every 6m distance, with installation of expansion joints each 12m (double columns), use of cork layers in the joints, with all the required works to complete the Job. Please see attached drawings
38 | Build The Walls Under D.P.C Layer | M3 | 15 |  | 0
Supply materials, tools and manpower to build the walls under D.P.C level with stone and cement-sand mortar (1:3) of 30 cm height the work includes smooth plastering the walls with cement –sand mortar (1:3), coating the buried foundations for both sides using the tar type II or III and backfilling the foundations sides with sub-base ''class C''. For more details, please see attached drawings.
39 | Sulphate Resistant plain Concrete for D.P.C Layer | M.l | 120 |  | 0
Supply materials, tools and manpower to cast the D.P.C layer of 10 cm thick and 21Mpa compressive strength, with all the required works to complete the Job.
40 | Build The Walls Above D.P.C Layer | M3 | 48 |  | 0
Supply materials, tools and manpower to build the block wall fence using hollow concrete block of (40x20x20) cm and cement –sand mortar (1:3), 2m height above the D.P.C, with all the required works to complete the Job. For more details, please see attached drawings.
41 | Plain Concrete for Cover Along The Wall | M3 | 5 |  | 0
Supply materials, tools and manpower to cast concrete cover of 10 cm thick, 40 cm width and 21 Mpa compressive strength along the block wall fence, with all the required works to complete the Job. For more details, please see attached drawings.
42 | Reinforced Concrete for Columns Doors | M3 | 2 |  | 0
Supply materials, tools and manpower to cast reinforced concrete columns of (40x60) cm with foundation of 1x 1 m, 0.5m depth and 24Mpa compressive strength for the doors.
43 | Smoothed Cement Plastering for The all Fence Walls | M2 | 650 |  | 0
Supply materials, tools and manpower for cement plastering with 20mm thickness smooth-finished for the fence wall, columns and concrete cover above the fence walls using aluminum straight edges. The price includes three layers as follows: one layer of cement splash dash, one layer of rough (kafmal) and finally smooth finished cement plastering with cement-sand mortar(1:3), putting a layer of metal mesh on the area under the cement plastering which should be installed at the linking area of the concrete columns with the block walls and all the required works to complete the work.
44 | Plastic Painting for The Fence Wall: Supply of materials, tools and manpower to paint the fence walls and concrete cover above the fence walls with three layers of external plastic (silicon water proof) paint (Jotun- Jotashield, Betek, CAPAROL, Polisan, dyo). The job includes cleaning the walls, removing the dirt and dust. All needed works to complete the job, shall be included within the price. | M2 | 650 |  | 0
45 | Wrought Iron Wall Railings for The Front Fence Wall: Supply and install steel wrought iron wall railing of 80 cm high for the front fence only that consist of steel square section for external frame for railing of 2 inch and 3 mm thick, steel square section frame around the steel plates sheets of 3/4 inch and 2 mm thick and steel plate sheet of 3 mm thick with the use of geometric engravings on the steel plates designed by CNC machines as per attached drawings, the work includes installing it between two concrete columns using steel base plate of 10 mm thick which should be installed in the concrete columns using rawl bolts, painting iron wall railings and base plate with 3 layers of oil based paints type hammer finish in addition to anti-rust primer and all the required works to complete the Job | M2 | 28 |  | 0
46 | Cladding The Concrete Columns for The Front Fence Wall:
Supply materials, tools and manpower for cladding the concrete columns for the front fence wall only with limestone panels type (Mosul - Ba'adhira) , price should include filling the spaces between the stone and the walls by using cement mortar (1:3) and the joints between stone with white cement and crushed stone powder (1:1), using solid copper wire for the installation of stone, polishing stone very well taking into account the special safety requirements, and according to the technical specifications and attached drawings as follows (The contractor should be complied with all forms and types of stone and all other details referred to in the attached drawings and designs) ,and all the required works to complete the works. As the following:
A | Stones panels with thickness of not less than 5 cm | M2 | 7 |  | 0
B | Stones Frame of 20 cm height ( Coplan- كوبلن صدر طير) | M.l | 8 |  | 0
C | Stones Frame of 20 cm height and 5 cm thick ( Coplan) | M.l | 8 |  | 0
D | Stones Frame of 15 cm height and 5 cm thick ( Coplan) | M.l | 70 |  | 0
E | Marble tiles of 2 cm thick and 30 cm height. | M2 | 11 |  | 0
C: Sanitary Works
Notes:
The items prices below should be included the following:
1- provision, installation, connection, operation and inspection of all the materials in their locations according instructions of the engineering committee, then testing the networks sanitary works, with all requirements to complete the job.
2- The work shall be according to the technical specifications and the materials shall be of high quality after submitting samples (at least 3 of Egyptian, Turkish or Saudi origin) for all materials of pipes and fittings to engineering committee.
3- All materials should be subjected to laboratory tests and may not use any material not tested.
4- When the PVC sewage pipes networks are established for a sanitary unit, they should be examined under appropriate pressure as per technical specifications.
5- The 35 cm height of the sanitary unit walls and floor should be Spread with two layers of tar and one layer of SBS modified bitumen waterproofing membrane of (Saudi or Jordanian origin) of 3mm thick.
6- Dumping of all debris to a site approved by local authorities.
7- All the requirements and accessories of the pipes feeder and fitting, connecting the building networks (pure water and sewage) with the source of water and drainage network. Sanitary works include the following:
47 | Septic Tank | Ea. | 1 |  | 0
Supply of materials, tools and manpower to build septic tank of (L=3.0m, W=5.0m and H=2.0m) dimension as per attached drawings. The price also includes soil excavations, casting the reinforced concrete foundation using (C21Mpa) Concrete, 20 cm thick and 40cm width using sulphate resistant cement, build the walls of 20 cm width with solid concrete block (15x20x30cm) and cement mortar (1:3), casting reinforced concrete slab (20cm) with two layers of 12mmØ spaced @20cm both directions and installation of two manhole hard plastic manhole covers of (60 x 60 ) cm . All needed work to complete the job will be included within the price.
48 | Installation and Connection of PVC pipes:
Supply, install, connect, testing and commissioning PVC pipes of SN8 drainage 6 bar from Egyptian origin , starting from fixtures down to manholes and septic tank, The work includes excavation (40x60cm), backfill, covering the pipes at the joints with concrete 10 cm from all sides using sulphate resistant cement with all installations and connections accessories and fittings, Elbows, Tees, PVC p trap, gully trap .. etc.), with all the required works to complete the Job. As following:
A | PVC Pipe of 6 inch diameter. | M.l | 30 |  | 0
B | PVC Pipe of 4 inch diameter. | M.l | 40 |  | 0
C | PVC Pipe of 3 inch diameter. | M.l | 12 |  | 0
49 | Cast Iron Ventilation Pipe for Septic Tank | M.l | 5 |  | 0
Supply materials, tools and manpower to install new cast iron ventilation pipe of 3-inch diameter for Septic tank, the works includes all required civil works and installation accessories, with all works to complete the job.
50 | Concrete Manholes:
Supply materials, tools and manpower to construct a fair faced concrete manholes using steel frame as below dimensions with plain concrete of 21 Mpa compressive strength and 10 cm thick for all works (Floor and walls) using sulphate resistant cement, the work includes soil excavations to any required depth, spreading two layer of sub-base layer “Class B” shall be applied in layers of 25 cm thick, watered, leveled and well compacted, with manhole hard plastic manhole covers, with all requirements to complete the job. As per below dimensions:
A | Manholes of 60 x 60 cm | Ea. | 6 |  | 0
B | Manholes of 40 x 40 cm | Ea. | 2 |  | 0
51 | Floor Drain: | Ea. | 6 |  | 0
Supply and install 4” PVC floor gully trap of 100mm diameter. Price to includes (15x15) double chrome plated cover, all required pipes and fitting to connect it with the main sewage pipes, excavation, concreting around pipes and gullies, which should be distributed according to the directives of the Engineering Committee and the attached drawings. All needed work to complete the job will be included within the price.
52 | Roof Drain pipes: | M.l | 40 |  | 0
Supply, installation, testing and commissioning 4" PVC pipe of 10 bar of Egyptian origin, properly fixed with brackets to the wall and the slab, complete with all fittings and accessories for draining rain water from the roof. With all required hanging accessories, fittings and vent caps and all the required works to complete the Job.
53 | Eastern style toilet: | Ea. | 2 |  | 0
Supply and Install ceramic eastern toilet of Turkish or Iranian origin of (50 x 60) cm dimension, White, complete with flush tank "kahramana type", fitting, stop, valve side tap and with water toilet mixer (hot & cool) with handheld shower of Turkish origin, all sewage and potable water pipes to connect it with networks, installing and connecting gully trap of 100mm diameter, toilet brush and holder and all the required works to complete the Job.
54 | Western style toilet: | Ea. | 1 |  | 0
Supply, install, connect and test western ceramic toilet of Turkish or Iranian origin, price should include fitting, stop, valve side tap and with water toilet mixer (hot & cool) with handheld shower of Turkish origin, all sewage and potable water pipes to connecting it with networks, with toilet brush and holder and all the required works to complete the Job.
55 | Ceramic wash basin: | Ea. | 4 |  | 0
Supply, install, connect and test white ceramic wash basin with stand of western, Turkish or Iranian origin, size (60 X 50) cm complete with all fittings, valves, gully-trap, all sewage and potable water pipes to connecting it with networks, the price also includes the water mixer- first class of Turkish origin with all connections and installations accessories, stainless steel toilet accessories ( soap basket, wall toilet paper holder, mirror of 35x50 cm dimension and any other necessary parts with all the required works to complete the Job.
56 | Galvanized Water Tank: | Ea. | 2 |  | 0
Supply and install galvanized steel gage 16 water tank of 2000 Lit. capacity and Cylindrical shape. Price to include concrete stand and, supported by steel base made with 50mm (2") angle shape, float ball valve, valves, fittings, vents, check valves, connecting the tanks with the water distribution network of building and main water, and all necessary works to complete job.
57 | PPR pipes:
Supply materials, tools and manpower to install, connect and test (PPR) pipes of Yugoslav or Serb origin for the distribution water network (cold and hot water pipes)with isolate all hot water pipes by using arm flex and thermal tape and concreting 10cm around the pipes and the pipes from and to the water heater and the pipe which connecting the water network of the building and the source of main water network , price should include all connection and installations accessories and fitting as 90 elbow, tee and valve...etc., the work include connecting the project portable water network with water main source of the region which the PHCC is located, installing the pipe in walls, roofs and floor, testing the water pipes network for the building as per technical specifications with all the required works to complete the Job. As shown below:
A | PPR pipes of 1 inch diameter | M.l | 100 |  | 0
B | PPR pipes of 3/4 inch diameter | M.l | 65 |  | 0
58 | Galvanized iron water pipes | M.l | 50 |  | 0
Supply, install and test galvanized water pipes "class A" SCH40 of 1 inch diameter to connect and transfer water from and to water tanks which should be installed on the building roof. The price includes all fittings and accessories such as 90 elbow, tee and valve...etc., the work include installing the pipe in walls, roofs and floors, excavation, backfilling, painting the pipes using 3 layers of anti-rust then isolate all hot water pipes by using arm flex and thermal tape and Teflon seal for connections of cold and hot water pipes and concreting 10cm around the pipes, all needed work to complete the job will be included within the price. As shown below:
59 | Taps: | Ea. | 6 |  | 0
Supply and connect chrome water taps 3/4". Price of the work shall include all water connections, all pipes and fitting to connecting it with water distribution network and the taps locations should be determined by the engineering committee inside and outside the building. All needed work to complete the job will be included within the price.
60 | Stainless Steel Double Bowl Sink: | Ea. | 1 |  | 0
Supply of materials, tools and manpower to install and commission of stainless steel double bowl sink (150x60cm). Complete with: chrome mixer for sinks of Turkish origin, waste outlet, tail piece, P-trap chrome, chrome plated 14mm and all required parts, gully –trap, fittings, valves, in addition to aluminum sink cabinet storage (Aluminum Countertop) which consist of aluminum frame, heavy section of 1.3 mm and width not less than 5.0 cm aluminum sections and aluminum panel lambri of Turkish origin, each aluminum countertop piece containing 3 doors with aluminum shelves inside. The work includes, connecting it with networks of sewage and potable water, all needed work to complete the job will be included within the price.
D: Electrical Works
Notes:
The items prices below should be included the following:
1- The works should be included the provision, installation, connection, operation and inspection of all the materials in their locations according instructions of the engineering committee, then testing the electrical network of the building, with all requirements to complete the job.
2- The work shall be according to the technical specifications and the materials shall be first class and original not commercial or imitative. The required brand for electrical cables, wires, electrical PVC conduits to pull the wires, fittings, galvanized steel electrical boxes for sockets and electrical switch of Gulf or Jordanian origin. Lighting fixtures (ceiling or walls), bulbs, electrical lamp holders, LED projects and flood lights, celling fans, electrical sockets, metal distribution board box and switches of English, French origin or equivalent. Main and sub distribution boards, MCCB and MCB circuit backers and MCB Distribution Boards with all their accessories of ABB, Schneider, Siemens or equivalent.
3- The electrical PVC conduits which will use to pull the wires of lighting fixtures and electrical sockets and switches..etc. should be installed inside the concrete roofs not on their outer surface.
4- The contractor shall submit samples of all materials before providing to be approved or rejected them by engineering committee.
5- All electrical works should be subjected technical specifications (please see attached).
61 | One Gang Switched Socket of 13 Amp Capacity | Ea. | 58 |  | 0
Supply, install, connect, test and commission electrical point with electrical Plug switch one gang of 13 Amp capacity using single copper wires of 4 mm2 and (1x2.5) mm2 for earthing which must be installed in the walls according to the heights mentioned in the attached drawings, the work includes supplying and installing galvanized steel electrical box, pulling wires inside PVC conduits and connecting it to MCB distribution board with all installation and connection accessories, and all the required works to complete the Job . Please see attached drawings.
62 | Two Gang Switched Socket of 13 Amp Capacity | Ea. | 18 |  | 0
Supply, install, connect, test and commission electrical point with electrical Plug switch two gang of 13 Amp capacity using single copper wires of 4 mm2 and (1x2.5) mm2 for earthing which must be installed in the walls according to the heights mentioned in the attached drawings, the work includes supplying and installing galvanized steel electrical box, pulling wires inside PVC conduits and connecting it to MCB distribution board with all installation and connection accessories, and all the required works to complete the Job . Please see attached drawings.
63 | Waterproof one Gang Switched Socket of 13 Amp Capacity and IP54 | Ea. | 5 |  | 0
Supply, install, connect, test and commission electrical point with electrical waterproof Plug switch one gang of 13 Amp capacity and IP54 using single copper wires of 4 mm2 and (1x2.5) mm2 for earthing which must be installed in the walls according to the heights mentioned in the attached drawings, the work includes supplying and installing galvanized steel electrical box, pulling wires inside PVC conduits and connecting it to MCB distribution board with all installation and connection accessories, and all the required works to complete the Job . Please see attached drawings.
64 | One Gang Switched Socket of 15 Amp Capacity | Ea. | 8 |  | 0
Supply, install, connect, test and commission electrical point with electrical Plug switch one gang of 15 Amp capacity using single copper wires of 4 mm2 and (1x2.5) mm2 for earthing which must be installed in the walls according to the heights mentioned in the attached drawings, the work includes supplying and installing galvanized steel electrical box, pulling wires inside PVC conduits and connecting it to MCB distribution board with all installation and connection accessories, and all the required works to complete the Job . Please see attached drawings.
65 | Double Pole Switch of 45 Amp with Neon | Ea. | 15 |  | 0
Supply, install, connect, test and commission electrical point with double pole socket of 45 Amp capacity and IP54 with neon for air conditioning devices and water heaters using single copper wires of 4 mm2 and (1x2.5) mm2 for earthing which must be installed in the walls according to the heights mentioned in the attached drawings, the work includes supplying and installing galvanized steel electrical box, pulling wires inside PVC conduits and connecting it to MCB distribution board with all installation and connection accessories, and all the required works to complete the Job . Please see attached drawings.
66 | Triple Pole MCB of 63 Amp Capacity | Ea. | 2 |  | 0
Supply, install, connect, test and commission electrical point with triple pole MCB of 63 Amp capacity for three phase air conditioning devices using single copper wires of 6 mm2 and (1*2.5) mm2 for earthing which should be installed in the walls according to the heights mentioned in the attached drawings, the work includes supplying and installing MCB plastic cover, pulling wires inside PVC conduits of 25 mm diameter and connecting it to MCB distribution board with all installation and connection accessories, and all the required works to complete the Job. Please see attached drawings.
67 | Electric bell | Ea. | 4 |  | 0
Supply, install, connect, test and commission electric bell 220VAC/5 W, Wall Mounting and the sound level to be ISO 9001:2000 , for voltage 230VAC to be 68 dB to 108 dB sound level at 2 ft. & 2900 Hz operating frequency with electrical switches of 10 Amp capacity(bell push switch), using single copper wires of 2.5 mm2 and (1*1.5) mm2 for earthing , the work includes supplying and installing galvanized steel electrical box, pulling wires inside PVC conduits and connecting it to MCB distribution board with all installation and connection accessories, and all the required works to complete the Job.
68 | Ceiling Fan and Exhaust Fan
Supply, install, connect, test and commission electrical installations with electrical switches of 10 Amp capacity according to the kind of gangs and ways for electrical switches which mentioned in the attached drawings, the electrical switches should be installed on the 120 cm height from ground level of the building using single copper wires of 2.5 mm2 and (1*1.5) mm2 for earthing , the work includes supplying and installing galvanized steel electrical box, pulling wires inside PVC conduits and connecting it to MCB distribution board with all installation and connection accessories, and all the required works to complete the Job. The electrical installations are as following:
A | Ceiling fan of 56 inch with Fan Speed Control Switch | Ea. | 16 |  | 0
B | Exhaust fan of 8 inch diameter with electrical switch of 10 Amp capacity | Ea. | 12 |  | 0
C | Exhaust fan of 12 inch diameter with electrical switch of 10 Amp capacity | Ea. | 3 |  | 0
69 | Lighting Fixtures
: Supply, install, connect, test and operate lighting fixtures with electrical switches of 10 Amp capacity according to the kind of gangs and ways for electrical switches which mentioned in the attached drawings, the electrical switches should be installed on the 120 cm height from ground level of the building using single copper wires of 2.5 mm2 for main wires from MCB Distribution Boards and single wires 1.5 mm2 for sub wires which feeding the lighting fixtures and earthing wires , the work includes supplying and installing galvanized steel electrical box, pulling wires inside PVC conduits and connecting it to MCB distribution board with all installation and connection accessories, and all the required works to complete the Job. The lighting fixtures are as following:
A | LED Ceiling Tiles Lights (LED Surface Lights) of 42 Watt, 6500K, 4200 Lumens and 60 x 60 cm dimensions | Ea. | 64 |  | 0
B | Waterproof LED Ceiling Light (LED Surface Lights) outdoor of 24 Watt, IP65, 6500K and 4200 Lumens | Ea. | 11 |  | 0
C | Waterproof LED Ceiling Light (LED Surface Lights) of 24 Watt, IP65, 6500K and 4200 Lumens for sanitary units | Ea. | 5 |  | 0
D | Modern waterproof outdoor wall lighting fixtures (Lantern) with Led bulb lights ( Economic Bulb) of 20 watt | Ea. | 23 |  | 0
E | Big modern outdoor wall lighting fixtures (Lantern) with Led bulb lights ( Economic Bulb) of 40 watt which should be installed on the columns of front fence wall with all installations and connections accessories | Ea. | 6 |  | 0
F | Outdoor LED flood light (Waterproof) of 200 Watt, It should be installed in the rooftop of the building . | Ea. | 6 |  | 0
70 | COB LED Street Light Fixture of 100 Watt | Ea. | 6 |  | 0
Supply, install, connect, test and commission COB LED street light fixture of 100 Watt, 2 COB and 12000 lm Lamp Luminous Flux with all installations and connections accessories which should be installed on the back and side walls for the fence, the work includes, supplying and installing galvanized pipe of 2-inch diameter that should be installed in the concrete columns during casting the columns consist of columns of 1.2 m and two arms of 1 m for each arm, and all the required works to complete the Job.
71 | Cables
Supply, Install, connect, test and commission cables, the price should include supplying, installing, testing, commissioning materials, workmanship, equipment, machinery, trenching, all installation and connection accessories, the work includes pulling the cables that will come out from distribution boards to out side the buildings underground with excavation of trench cables path not less than 70 cm depth, spreading 30 cm river sand bedding around the cables, spreading the rest of trench depth with sub-base layers " Class B"with well compaction in layers so that the thickness of each layer does not exceed 20 cm, putting Underground Warning Tape along cables path, pulling the cables inside the PVC pipe of 10 bar in areas that intersect with the cars crossing areas and covering the pipe with 0.3 m plain concrete cover and pulling the cables that must feed the distribution boards inside the PVC pipes which should be installed in the walls well with excavation works for the pipe trench in the wall with plain concrete cover. The cables must be one length from the electric feeding sources to the electrical distribution boards, ie, it is not permissible to make joints when laying the cables, with all the required works to complete the Job.This items includes the cables shown below
A | Armored cable of (4x95) mm²+(1x50) mm² to feed the main distribution board for the project from the ATS, in addition to feed the ATS from electrical distribution board of the transformer and from the generator to ATS | M.l | 40 |  | 0
B | Unarmored cable of (4x25) mm²+(1x16) mm² to feed the MCB Distribution Boards P1, P2 and SP3 which are shown in attached drawings from the main distribution board of the project. | M.l | 60 |  | 0
C | Armed 4x6 mm2 to feed the sub distribution boards of the external lighting which should be installed outside the building in the area determined by the supervisory committee from main distribution board of the treatment unit. | M.l | 30 |  | 0
D | Flexible cable of 2x6 mm2 to feed the outdoor lighting Fixtures distributed around fence wall and from sub distribution boards of the external lighting. | M.l | 150 |  | 0
72 | Galvanized Cable Trays
Supply, install galvanized cable tray of the dimensions are shown below and plate thickness not less than 1.0 mm, which should be installed above false ceiling of the building using rawl polts to install and lay all cables on smoothly which feeding building parts as per attached drawings and according to the supervisory committee directions, with all the required works to complete the Job. As following:
A | Galvanized cable tray of W20 x h5 cm | M.l | 25 |  | 0
B | Galvanized cable tray of W10 x h5 cm | M.l | 12 |  | 0
73 | Manhole | Ea. | 3 |  | 0
Supply materials, tools and manpower to build manhole of (30x30x30)cm dimension using bricks and cement mortar (1:3) the work includes plastering using cement- sand mortar (1:3) and installation of hard plastic cover of 40x40 cm with all the required works to complete the Job.
74 | 24 Ways MCB Distribution Boards | Ea. | 3 |  | 0
Supply, install, connect, test and commission of 24 ways, TP + N bus bar type distribution board Combination bus bar and Din Rail, 2 row, 24 ways. of modules (distance between rows 150mm), contain of earth leakage circuit breakers for water heaters, with single door complete with accessories and separate neutral strip to accommodate incoming miniature circuit breaker (MCB) triple pole and 100 Amp capacity with bus bar of 150 Amp and outgoing SP MCBs, with all installations and connections accessories and all the required works to complete the Job.
75 | Main Distribution Board (MDB) | Ea. | 1 |  | 0
Supply, install, connect, test and commission prefabricated metal Main distribution board (MDB) of 120 cm x 80 cmx 40cm dimensions with metal stand, the work includes installing and connecting the digital screens for Ammeter, voltage and frequency meters with labels and all internal and external connection and installations accessories (connections, cables, fuses, phase, neutral and earthing bars, Isolators...etc.), and all the required works to complete the Job, which consist of:
A-1 Main circuit breaker of three phase and 250 Amp , 380 Vol ;
B- 3 MCCB 3PH 380 Vol, 100 Amp;
C-1 MCCB 3PH 380 Vol, 63 Amp;
D- 2 MCCB 3PH 380 Vol, 100 Amp (spare parts);
E- Set bus bar 3 PH 380 Vol,400 Amp and sub-busbar strips with different capacities according to the circuit breakers capacities in the MDB;
F-1 Three pole, LED Digital Voltage, frequency and Amperage meter with CT;
G-3 Indicator lamp 220VAC for each phase;
H- 2 Timer
I- 1 Phase failure
76 | Sub Distribution Boards of the External Lighting: | Ea. | 1 |  | 0
Supply, install, connect, test and commission prefabricated metal sub distribution board 50 cmx 40cm dimensions which is used to control the external lighting of the fence wall and which should be installed outside the building in the area determined by the supervisory committee, consist of main (MCCB) 3PH380 Vol, and 40 Amp, contactor of 40 Amp, selector switch Auto- Manual (M-O-A), photocell with all its accessories and four circuit breakers single phase (MCB) of 30 Amp capacity. All connection and installation accessories, labels and indicator lamps with all the required works to complete the Job.
77 | Three Phase Electric Meter | Ea. | 1 |  | 0
Supply, install, connect, test and commission three phase electric meter of German origin which must be subjected to the specifications of the Iraqi Ministry of Electricity, the price should include, installing it inside a waterproof metal board of suitable size for the size of the meter and in the place determined by the supervisory committee, all required cables, wires, fittings, terminal, all installation and connection accessories according to the supervisory committee directions, and all the required works to complete the work.
E: Mechanical Works
78 | Air-Conditioning Split Units
Supply, install, connect and test air-conditioning split units as per capacities shown below, heating and cooling, the compressor type T3 rotary compressor and gas type "Freon gas R410A", and wall type, the work includes, supplying, installing and connecting drain pipes inside the walls using PPR pipe of 3/4 inch with all required fittings to the nearest drain point, all required sleeve pipes from PVC pipe of 3 Inch diameter with all required fittings which should be installed in the walls and during cast the slab to connect the all the refrigerant piping to the condensing unit from indoor unit to outdoor unit which should be installed on the roof. The price should include, all the refrigerant piping to the condensing unit (from indoor unit to outdoor unit), all wiring, electrical controls, a steel base stand and steel sunshade for the outdoor unit, protection devices and all installation and connection accessories required, the required brand is Tosot or York. For more details, please see attached the Compliance sheet.
A | Air-Conditioning split units of 1.5 Ton capacity | Ea. | 5 |  | 0
B | Air-Conditioning split units of 2 Ton capacity | Ea. | 7 |  | 0
79 | Air-Conditioning Split Units of 3 Ton Capacity | Ea. | 1 |  | 0
Supply, install, connect and test air-conditioning split units of 3 Ton capacity, heating and cooling, the compressor type T3 rotary compressor and gas type "Freon gas R410A", floor standing type, the work includes, supplying, installing and connecting drain pipes inside the walls using PPR pipe of 3/4 inch with all required fittings to the nearest drain point. The price should include, all the refrigerant piping to the condensing unit (from indoor unit to outdoor unit), all wiring, electrical controls, a steel base stand for the outdoor unit, protection devices and all installation and connection accessories required, the required brand is Tosot or York. For more details, please see attached the Compliance sheet.
80 | Air-Conditioning Split Units of 4 Ton Capacity | Ea. | 2 |  | 0
Supply, install, connect and test air-conditioning split units of 4 Ton capacity, heating and cooling, floor standing type and three phase, the compressor type T3 rotary compressor and gas type "Freon gas R410A", the work includes, supplying, installing and connecting drain pipes inside the walls using PPR pipe of 3/4 inch with all required fittings to the nearest drain point. The price should include, all the refrigerant piping to the condensing unit (from indoor unit to outdoor unit), all wiring, electrical controls, a steel base stand for the outdoor unit, protection devices and all installation and connection accessories required, the required brand is Tosot or York. For more details, please see attached the Compliance sheet.
81 | Electrical Water Heater | Ea. | 2
Supply, install, connect, and commission electrical heater of 160 Liter capacity. The price includes supplying, installing, connecting, laying and commissioning drilling, cutting, all pipes, fitting, valves, check valves, relief valves and steel base and connect it with the electrical source using cable (3*2.5) mm2, with all the required works to complete the Job.
82 | Water Pump: | Ea. | 1 |  | 0
Supply, install and connect water pump with motor(1.1 kW, 220 V, 50 Hz ), Q=3 m3/Hr@ H=15 m. check valve and strainer for connecting the pump suction pipe to the main water source pipe and connecting the discharge of the pump with pipe going up to the tanks, also the pump should have pressure switch on the pump for shut down the pump when the tank is filled . The work includes all connection and installation accessories, pipes, fitting and the electrical connection using 1.0 kV grade PVC insulated copper cable 2x2.5 mm² with main cable with all accessories to complete work as required.
F: Systems of Fire Detection and Alarm, Telephone, TV, CCTV and Earthing
83 | Fire Detection and Alarm System.
Supply, Install, connect, test and commission an analogue addressable fire-alarm control panel included of all equipment and accessories, batteries, battery charger, internal conductors and/or cables, switches, spare parts and warranty for 3 years, the Fire alarm detector point, Complete with steel conduits, boxes, junctions, FPLR fire resistance cable (2X1.5 mm2+0.8mm) and all accessories, from fire alarm panel to addressable detector or break glass fire call point, the required brand is English, German or French origin. Certificate of origin or BV inspection are required, as specified according to technical specification, please see attached drawings.
A | Main Fire Alarm Control and Annunciator Cabinet ( 1 Loop) | Ea. | 1 |  | 0
B | Smoke Detector | Ea. | 16 |  | 0
C | Flasher with Siren | Ea. | 2 |  | 0
D | Break glass pushbutton switch or manual call point. | Ea. | 2 |  | 0
84 | Telephone Central System
Supply, Install, connect, test and commission telephone central system for the telephone communication as specified according to technical specification. Please see attached drawings, which including the following:
A | Supply, Install, connect, test and commission automatic electronic telephone central system of 20 internal lines and 2 external lines which must include all required telephone cables from MDF with it, all accessories, necessary connections and installations, with wooden desk of 180cm length and UPS of 3000VA capacity. The required brand is English, French or Japanese origin, with all the required works to complete the Job | Ea. | 1 |  | 0
B | Supply, install, connect and test high quality main telephone destitution board (MDF) of 32 lines which should be installed in the walls, with all installation and connection accessories, with all the required works to complete the Job. | Ea. | 1 |  | 0
C | Supply, install, connect, test and operate 1 Gang RJ11 Phone Socket which should be installed on the 45 cm height from ground level of the building using telephone wire of 2 pair. The work includes all wires (from sockets until the MDF), supplying and installing galvanized steel box (J- box), PVC conduits which should be installed above false ceiling of the building pulling wires inside PVC conduits in the walls with all installation and connection accessories, and all the required works to complete the Job. | Ea. | 12 |  | 0
D | Telephone desktop set of Japanese origin with LCD display and Caller ID display facility with wooden table of 78 cm height and 50x 50 dimensions , the required brand Sonny | Ea. | 12 |  | 0
85 | TV System
Supply, Install, test and commission TV system, the required brand is English, French, Japanese or equivalent, as specified according to technical specification:
A | Satellite Socket | Ea. | 4 |  | 0
Supply, install, connect, test and operate single satellite socket wall plate which should be installed on the 45 cm height from ground level of the building using high quality RG6 coaxial cable. The work includes all cables (from socket to the dish), laying the cables, supplying and installing galvanized steel box (J- box), pulling wires inside PVC conduits in the walls with all installation and connection accessories, and all the required works to complete the Job.
B | Receiver Dish Satellite | Ea. | 1 |  | 0
Supply, install, connect and test high quality receiver dish satellite of 1.5m diameter with quad LNB of four outputs ASWAR Type, dish steel stand and all its accessories, and all the required works to complete the Job
86 | CCTV System Points | Ea. | 12 |  | 0
Supply materials, tools and manpower to install CCTV system points which will be distributed on site as per attached drawings and supervisory committee directions to cover the project areas, the work include supplying, installing and connecting thick waterproof PVC square junction box for CCTV cameras of IP65 and12 x12 cm dimensions , RG59 coaxial CCTV cable with VDE power cable which should pull in PVC conduits from determined camera point to the metal board inside the reception or any room determined by the supervisory committee ( this PVC conduits should be installed above false ceiling) and metal board of 50 x 50 cm, single airtight door with lock which should be installed inside the wall to be assembled all cables inside it, the cables must be one length from the camera box to the metal board, i.e., it is not permissible to make joints when laying the cables. The price should include, marking or number each cable with its camera box, all installation and connection accessories, all required fittings. All needed work to complete the job will be included within the price.
87 | Earthing system: | Ea. | 1 |  | 0
Supply, install and connect earthing system for the building consists of three copper rods( each length 1.5 m, 16 mm dia), connected together by copper wire of (1 x25) m² to form triangle shape ( on the surface/ground with each side length of 3 m from each other and copper wire buried at 2 m deep). work include the excavation of three earthing pit ( depth of 2m each) .The price includes supplying, installing, connecting, laying and commissioning drilling, cutting, digging/excavating and backfilling with mixture of layers (sand, salt and charcoal) and all the required works to complete the Job.
G: Supplying The PHCC with an Electrical Current from Main Electrical Source
88 | Electrical Transformer of 250 kVA capacity | Ea. | 1 |  | 0
Supply, install, connect, test and commission electrical transformer of 11/0.416 kV and 250 kVA capacity, Turkish or KSA origin, compatible with the Ministry of Electricity specifications- transformer technical specification IEC-60076 with all electrical connection and installation accessories. certificate of origin and inspection documents are required. For more details, please see Annex A (D-26).
89 | Electrical Distribution Board | Ea. | 1 |  | 0
Supply, install, connect, test and commission low voltage electrical distribution board of 400V capacity consist of metal box, circuit breaker of 3 phases and 250 Amp capacity, busbars, voltage/amperage meters, clands and all accessories, preferred brand is ABB, Schneider or Siemens; the metal box must be suitable to be fixed on tubular pole, waterproofing. The electrical distribution board and its accessories should be suitabled to operate under heavy load and short circuit system. For more details, please see Annex A (D-09).
90 | Galvanized Tubular Steel Pole of 11m height | Ea. | 2 |  | 0
Supply and install galvanized tubular steel pole of Turkish origin and 11m height, the work includes excavation in any soil type, spreading two layer of sub-base layer “Class B” shall be applied in layers of 25 cm thick, watered, leveled and compacted and one layer of thick agricultural nylon of 1 mm, casting the concrete base of the pole of 40 x 40 x 210 cm dimensions with plain concrete of 21 Mpa compressive strength using steel mold, coating the concrete base from all sides with two layers of liquid bitumen primer for waterproofing (flancote), filling the sides of the excavation using compacted sub-base layers class B, with all connection and installation accessories and all the required works to complete the work. For more details, please see Annex A (D-22).
91 | Galvanized Lattice Steel Pole of 11m height | Ea. | 0 |  | 0
Supply and install galvanized Lattice steel pole of Turkish origin and 11m height, the work includes excavation in any soil type, spreading two layer of sub-base layer “Class B” shall be applied in layers of 25 cm thick, watered, leveled and compacted and one layer of thick agricultural nylon of 1 mm, casting the concrete base of the pole of 40 x 80 x 210 cm dimensions with plain concrete of 21 Mpa compressive strength using steel mold, coating the concrete base from all sides with two layers of liquid bitumen primer for waterproofing (flancote), filling the sides of the excavation using compacted sub-base layers class B, with all connection and installation accessories and all the required works to complete the work. For more details, please see Annex A (D-46).
92 | Steel Channel of 220 cm length | Ea. | 3 |  | 0
Supply, install and connect heavy steel channel of 220 cm length (for transformer base and expulsion fuse cutout fixation) with clamps and screws, the channel must have suitable holes and be painted with two layers of anticorrosion paint and two layers of silver oily paint and as per the specifications of the Ministry of Electricity.
93 | Expulsion Fuse Cutout of 11 KVa | Set | 1 |  | 0
Supply, install, connect, test and commission expulsion fuse cutout of Turkish origin and 11kVa capacity, with all connection and installation accessories and all the required works to complete the work. For more details, please see Annex A (D-25).
94 | Earth Rod Copper Bar | Ea. | 1 |  | 0
Supply, install and connect earth rod copper bar of 1/2 inch diameter and 1.5m length with clamp, with all connection and installation accessories and all the required works to complete the work and as per the specifications of the Ministry of Electricity.
95 | Copper Conductor of 70 mm | M.l | 20 |  | 0
Supply, install and connect copper conductor of 70 mm2 to connect between transformer and earth rod copper bar, with all connection and installation accessories, cable terminals (lugs) and all the required works to complete the work. For more details, please see Annex A (D-47).
96 | Surge Arrester of 11 kV capacity | Set | 1 |  | 0
Supply, install and connect surge arrester of Turkish origin and 11 kV capacity, with all connection and installation accessories and all the required works to complete the work. For more details, please see Annex A and as per the specifications of the Ministry of Electricity.
97 | PVC insulated Single Core LV Cu Cable of 1x120 mm2 | M.l | 22 |  | 0
Supply, install and connect PVC insulated single core LV Cu cable of 1x120 mm2 of Turkish origin to connect between the transformer and the electrical distribution board under the transformer, with all connection and installation accessories, cable terminals (lugs) and all the required works to complete the work. For more details, please see Annex A.
98 | Pin Insulator with Spindle of 11kVA Capacity | Ea. | 2 |  | 0
Supply, install and connect pin insulator with spindle of Turkish origin and 11kVa capacity, with all connection and installation accessories, bolts and all the required works to complete the work. For more details, please see Annex A (D-24).
99 | Disk Insulator of 11kVA Capacity | Ea. | 10 |  | 0
Supply, install and connect disk insulator of Turkish origin and 11kVA capacity with its accessories (couple disks of 11kVA with the ring, socket A, A and U bolt),with all connection and installation accessories, and all the required works to complete the work. For more details, please see Annex A and as per the specifications of the Ministry of Electricity.
100 | AAC Conductor of (95) mm2 | M.l | 150 |  | 0
Supply, install, connect, test and commission all aluminum conductor (AAC) of (95)mm2, with all connection and installation accessories, terminals and all the required works to complete the work. For more details, please see Annex A (D-47).
H: Supply, Installation and Connection of New Generators for PHCC
101 | Generator of 150 kVA Capacity | Ea. | 1 |  | 0
Supply, install, connect, test and operate generator of 150 kVA capacity (50Hz/400V) silent type and 6 cylinders, the required brand is Perkins or caterpillar, the work includes supplying, installing and connecting galvanized fuel tank(Cylindrical shape) of 3,000 ltr capacity to be installed on concrete base with all the required accessories and connectors, with all requirements to complete the job. Certificate of origin and inspection documents are required. For more details, please see attached the technical specifications and compliance sheet.
102 | Automatic Transfer Switch (ATS) of 630 Amp Capacity | Ea. | 1 |  | 0
Supply, install, connect, test and operate automatic transfer switch (ATS) of three phase and 630 Amp capacity with the metal board of 80x40x30 cm size, pass bars, timers, relays, cables, control switchboard and multi digit screens (V, A, Hz). Preferred brands are ABB, Schneider, Siemens, with steel frame to install the metal board, all electrical installation and connection accessories, and all the required works to complete the Job.
103 | Concrete with BRC for Generator Base Floor | M2 | 16 |  | 0
Supply materials, tools and manpower to cast the generator floor, the work includes leveling the ground, compaction of existing soil, spreading sub-base layer compacted with 95% degree of compaction and 25 cm thick, spreading thick agriculture nylon layer and casting with compressive strength 21 Mpa reinforcement sulphate resistance concrete with BRC layer of 6 mm thick, smooth surface and 15 cm thick using Helicopter for leveling concrete surface, the price should include making expansion joints every 4m both directions , according to the mentioned places in the attached drawings and all the required works to complete the work.
104 | Generator Metal Sunshade Works | M2 | 16 |  | 0
supply materials, tools and manpower to install metal sunshade roof above the generator of 2.5m height, according to details below:
- Steel square column of 3x3 inch and 4 mm thick and the distance from column and another should not be more than 3 m.
- Base plate of 25x25 cm dimension10 mm thick to install the sunshade steel structure with concrete base floor using rot bolts of 18 mm diameter with all required works
- Steel hollow square section for beams of roof structure of 3x3 inch dimensions and 4 mm thick.
- Steel hollow rectangular section for sub beam 1.5x3 inch and 3 mm thick.
- 0.8mm thick corrugated plates for the roof, fixed by screws and overlapped in order to prevent water leakage.
The work includes all cutting and welding works, painting with anti-rust and three layers of oil paint for all steel structure with all the required works to complete the Job.
I: Gardens Works
105 | Supply materials, tools and manpower to backfill the garden with clean soil and planting it as per the supervisory committee directions, the work includes the following:
A | Backfilling with clean, blended and screened Loam soil layer in addition to free of impurities and salts of 40 cm thick. | M3 | 100 |  | 0
B | Supply and install concrete garden edge for the front garden of (75 cm) length and (35 cm) height with well installation using cement- sand mortar, the work includes painting using one layer of plastic based paint and three layers of oil based paints, and all the related accessories required to complete the Job | M.l | 100 |  | 0
C | Supplying and planting American natural grass, It should be supplied in the form of pieces of 35x35 cm dimensions, each 2 pieces are divided into small pieces to cover 1m2 area | Piece | 100 |  | 0
D | Supplying and planting the palm trees with not less than 2m length. | E.a | 10 |  | 0
E | Supplying and planting the ficus tree with not less than 1.5m length. | E.a | 10 |  | 0
F | Supplying and planting Rose flowers with not less than 1.m length. | E.a | 30 |  | 0
Total Cost $ |  |  |  |  | 0