## Sheet1
Full Scale Rehabilitation of Al-Atifah Primary School for Girls and Boys (12 Classes) in Al-Qaim
Item # in BOQ | Item | Description | Required Specifications | Offered Specifications
B: Reconstruction of The Classrooms Building
B1: Civil Works
B1-6: Doors,Windows, Handrail, Ladder and Sun Shed works
23 | Roller Curtains | Origin: | Turkish Origin or equivalent
A- Fabric:
|  | Available in a variety of solar screen, light filtering, and room darkening fabrics. | Available in a variety of solar screen, light filtering, and room darkening fabrics.
|  | Dual shade systems require two fabric selections. Typically one blackout and one solar screen. | Dual shade systems require two fabric selections. Typically one blackout and one solar screen.
B-Clutch Mechanism:
|  | Shall be made in corrosion resistant plastic and internal mechanisms of Nylon 6 construction. Shall consist of a heavy duty single wrap spring that creates a positive mechanical relationship between the roller shade tube unit and the universal installation brackets to ensure stationary positioning in the static state. When activated the wrap spring releases and permits the clutch to turn while reducing friction on the clutch. The clutch will be press fit into the tube with ribs that engage with the tube’s internal locking channels. The chain control will be available on either the right or the left side of the shade. Clutch End Locking System: The clutch shall have a locking system which prevents the shade from coming out of its brackets if the shade is operated incorrectly. | Shall be made in corrosion resistant plastic and internal mechanisms of Nylon 6 construction. Shall consist of a heavy duty single wrap spring that creates a positive mechanical relationship between the roller shade tube unit and the universal installation brackets to ensure stationary positioning in the static state. When activated the wrap spring releases and permits the clutch to turn while reducing friction on the clutch. The clutch will be press fit into the tube with ribs that engage with the tube’s internal locking channels. The chain control will be available on either the right or the left side of the shade. Clutch End Locking System: The clutch shall have a locking system which prevents the shade from coming out of its brackets if the shade is operated incorrectly.
|  | Dual shade systems utilize two clutches. Chain controls can be positioned both right, both left, or one right and one left. | Dual shade systems utilize two clutches. Chain controls can be positioned both right, both left, or one right and one left.
B4: Mechanical Works
40 | Air-Conditioning Split Units of 2 Ton Capacity | Manufacturer Name: | Tosot , York or equivalent which should be approved by the supervisory committee before starting supplying process
|  | Type: | Heating and cooling and Wall Mounted Split Unit
|  | Auxiliary supply voltage (V): | 230 V/50HZ
|  | Tonnage Range (T): | 2 Ton
|  | Compressor: | Rotary / T3
|  | Refrigerant Gas: | R410A
|  | Cooling and Heating Capacity (BTUH): | 24000
|  | Filter Type: | Micro dust protection filter washable
|  | Running current (A): | As Manufacture
|  | Operation Range temperature ©: | 17 -30
|  | Remote Control: | Wireless /LCD type
|  | Noise Level (dB): | 30 - 35 -40
|  | Max ambient temp.: | T3 (52°C)
|  | Certification of origin: | Yes/Required
|  | Submit Manufacturer certification and test reports: | Yes/Required
|  | Submit Detail drawing brochure catalogue.: | Yes/Required
C - Rehabilitation of the Administration and Sanitary Buildings
C1-Civil Works
C-1-4: Doors,Windows, Ladder and Sun Shed works
64 | Roller Curtains | Origin: | Turkish Origin or equivalent
A- Fabric:
|  | Available in a variety of solar screen, light filtering, and room darkening fabrics. | Available in a variety of solar screen, light filtering, and room darkening fabrics.
|  | Dual shade systems require two fabric selections. Typically one blackout and one solar screen. | Dual shade systems require two fabric selections. Typically one blackout and one solar screen.
B-Clutch Mechanism:
|  | Shall be made in corrosion resistant plastic and internal mechanisms of Nylon 6 construction. Shall consist of a heavy duty single wrap spring that creates a positive mechanical relationship between the roller shade tube unit and the universal installation brackets to ensure stationary positioning in the static state. When activated the wrap spring releases and permits the clutch to turn while reducing friction on the clutch. The clutch will be press fit into the tube with ribs that engage with the tube’s internal locking channels. The chain control will be available on either the right or the left side of the shade. Clutch End Locking System: The clutch shall have a locking system which prevents the shade from coming out of its brackets if the shade is operated incorrectly. | Shall be made in corrosion resistant plastic and internal mechanisms of Nylon 6 construction. Shall consist of a heavy duty single wrap spring that creates a positive mechanical relationship between the roller shade tube unit and the universal installation brackets to ensure stationary positioning in the static state. When activated the wrap spring releases and permits the clutch to turn while reducing friction on the clutch. The clutch will be press fit into the tube with ribs that engage with the tube’s internal locking channels. The chain control will be available on either the right or the left side of the shade. Clutch End Locking System: The clutch shall have a locking system which prevents the shade from coming out of its brackets if the shade is operated incorrectly.
|  | Dual shade systems utilize two clutches. Chain controls can be positioned both right, both left, or one right and one left. | Dual shade systems utilize two clutches. Chain controls can be positioned both right, both left, or one right and one left.
C4: Mechanical Works
96 | Air-Conditioning Split Units of 2 Ton Capacity | Manufacturer Name: | Tosot , York or equivalent which should be approved by the supervisory committee before starting supplying process
|  | Type: | Heating and cooling and Wall Mounted Split Unit
|  | Auxiliary supply voltage (V): | 230 V/50HZ
|  | Tonnage Range (T): | 2 Ton
|  | Compressor: | Rotary / T3
|  | Refrigerant Gas: | R410A
|  | Cooling and Heating Capacity (BTUH): | 24000
|  | Filter Type: | Micro dust protection filter washable
|  | Running current (A): | As Manufacture
|  | Operation Range temperature ©: | 17 -30
|  | Remote Control: | Wireless /LCD type
|  | Noise Level (dB): | 30 - 35 -40
|  | Max ambient temp.: | T3 (52°C)
|  | Certification of origin: | Yes/Required
|  | Submit Manufacturer certification and test reports: | Yes/Required
|  | Submit Detail drawing brochure catalogue.: | Yes/Required
97 | Electrical Water Heater 160 Liter capacity | Type: | Electrical water boiler 160 liter with heater 3000Wat
|  | Installation: | Vertical /Cylindrical
|  | Water Tank Coating: | Enameled
|  | Capacity Range: | 160 Liter
|  | Electric heating type | Two Immersion element of 3000 Watt Italian origin or equivalent
|  | The thickness of internal basin walls | Not less than 2.5 mm
|  | Nominal power: | 220v-240v /50HZ
|  | Nominal pressure: | 0.8 Mpa
|  | In let & out let Decimeter: | ¾ “Inch
|  | Electric heating type: | Immersion element
|  | Insulation Type: | Foam
|  | Protection: | Safety Valve ¾”
|  | Submit Manufacturer certification and test reports: | Yes/Required
|  | Submit Detail drawing brochure catalogue: | Yes/Required
98 | Water pump | Origin : | Western origin or equivalent
A-Motor:
|  | Rated voltage: | 220V – 240V
|  | No of phase: | 1PH with capacitor
|  | Frequency: | 50 Hz
|  | Rated speed: | 2900 RPM
|  | Rated power: | 1.1 Kwatt
|  | Cos phi power factor: | 0.80 - 0.90
|  | Start method: | Normal Start
|  | Enclosure class: | (IEC 34-1)( protect water jet, mud and dust)IP 55
|  | Insulation class: | F
|  | Motor Protect: | Full motor protection
|  | Thermal Protection: | Full motor protection
|  | Built-in temperature transmitter: | Yes
|  | Max ambient temp.: | 60°C
B- Pump section
|  | Type: | Centrifugal horizontal Pump electrically controlled
|  | Pump liquid: | Clean water
|  | Rated flow: | 3m3/hr.
|  | Rated head: | 15 M
|  | Pump Body: | Cast Iron with threaded ports ISO 228/1
|  | Shaft Materials: | Stainless Steel 1.4404
|  | Impeller Material: | Brass, radial Peripheral Vanes.
99 | Stainless Steel Water Cooler | Type: | Free standing Cold Drinking Water Dispenser
|  | Brand | Al Sabeel or equivalent
|  | Capacity: | 90 Litter
|  | Cooling water capacity : | 90 Litter per hour up to 5 Degrees
|  | Material of Tank: | Stainless steel 316
|  | Dip Tray: | Stainless steel 304
|  | Number of Taps: | 4 Taps
|  | Type of Tap: | Push cocks
|  | Compressor Capacity: | 1/2 HP
|  | Type: | Rotary
|  | Refrigerant Gas: | R410a
|  | Voltage: | 220v -240v/50HZ
|  | Certification of origin: | Yes/Required
|  | Submit Manufacturer certification and test reports: | Yes/Required
100 | 7 Stage RO Filter | Origin: | Taiwanese origin or equivalent
Consist of:
|  | One 5 Micron Polypropylene Sediment Filter PP. | One 5 Micron Polypropylene Sediment Filter PP.
|  | One Granule Activated Carbon Filter (GAC) - Chlorine and Lime. | One Granule Activated Carbon Filter (GAC) - Chlorine and Lime.
|  | One 1 Micron Activated Carbon Block Filter (CTO). | One 1 Micron Activated Carbon Block Filter (CTO).
|  | One Fullcome Membrane 50 GPD - 0,0001 Micron. | One Fullcome Membrane 50 GPD - 0,0001 Micron.
|  | One Post Inline Carbon Filter. | One Post Inline Carbon Filter.
|  | One Alkaline Re-Mineralization Filter. | One Alkaline Re-Mineralization Filter.
|  | One UV Sterilization Filter. | One UV Sterilization Filter.
|  | One Storage Tank 10 Liters, RO Pipe 5 Meters, Connection fitting 15mm. | One Storage Tank 10 Liters, RO Pipe 5 Meters, Connection fitting 15mm.
F: Supplying The School with an Electrical Current
118 | Transformer 11/0.416 kV 250 KVA | 1-Make/Brand/Model: | To be filled in
|  | 2-Name of manufacturer | To be filled in
|  | 3-Type: | Oil-immersed hermetically sealed - bolted type
|  | 4-Country of origin | Turkish , KSA origin or equivalent which should be approved by the supervisory committee before starting supplying process
|  | 5-Reference standard | IEC 60076-1, 2,3,5,8, IEC 60214, IEC 60137
|  | 6-Ambient temperature: | Maximum:55/C Minimum: -10/C
|  | 7-Air humidity: | 92% maximum
|  | 8-Altitude: | 1000M above MSL
|  | 9-Number of poles | 3
|  | 10-Indoor or outdoor | Outdoor
|  | 11-Highest system voltage | 12 kV
|  | 12-Short circuit current on 11 kV side | 25 KA
|  | 13-Short circuit current on LV side | To be filled in
|  | 14-11 kV system earthing | Neutral isolated / earthed through a resistor
|  | 15-Low voltage side earthing | Neutral solidly earthed
|  | 16-Voltage Ratio | 11/0.416 KV
|  | 17-Type of cooling | ONAN
|  | 18-Rated power - Continuous | 250 kVA
|  | 19-Rated Frequency | 50Hz
|  | 20-Altitude: | 1000M above MSL
|  | 21-Impedance voltage at 75 deg at nominal tap | 4%
22-Nominal Voltage of winding
|  | a) H.V. | 11 kV
|  | b) L.V | 0.416 kV
23-Insulation level 11 kV
|  | a) Lightning Impulse | 75 kV
|  | b) AC power frequency | 28 kV
|  | 24-A- Insulation level LV -phases/neutral | To be filled in
|  | B-AC power frequency | 3 V
|  | 25-Short circuit withstand capacity of transformer | …..KA for …….seconds
|  | 26-Winding temperature rise at rated power | 50 C
|  | 27-Top oil temperature rise at rated power | 45 C
|  | 28-No load loss in | ……..KW
|  | 29-Load loss at full load at 75 deg temperature | ……..KW
|  | 30-Guaranteed magnetizing current | ……….A
|  | 31-Maximum flux density in iron at rated frequency and at rated voltage ratio at nominal voltage | ≤ 1.65 Tesla
32-Maximum current density in windings at rated power
|  | a) H.V. winding | To be filled in
|  | b) L.V. winding | To be filled in
|  | 33-Zero sequence impedance | To be filled in
|  | 34-No load current at rated voltage | …A
|  | 35-Material of windings | Copper
36-Type of winding
|  | a) H.V. | To be filled in
|  | b) L.V. | To be filled in
37-Type of insulation of winding
|  | a) H.V. | To be filled in
|  | b) L.V. | To be filled in
38-Type of insulation of
|  | a) Core assembly | To be filled in
|  | b) Core laminations | To be filled in
39-Thickness of transformer
|  | a) tank | Minimum 3 mm
|  | b) sides | Minimum 3 mm
|  | c) bottom | Minimum 3 mm
|  | 40-Thickness of radiator plates and for cooling tube | ….. mm
41-Winding connection
|  | a) H.V. | Delta
|  | b) L.V. | Star (Neutral brought out)
|  | 42-Vector group symbol | Dyn11
|  | 43-Type of core | To be filled in
|  | 44-Core sheet materials | To be filled in
|  | 45-Tap changer | Off-load tap changer with 5 positions in the HV winding giving ± 2 x 2.5 %.
|  | 46-11 kV side terminal arrangement | Clamp type for terminating up to 150 mm2 copper conductor
|  | 47-Low voltage terminal arrangement | Suitable for terminating copper cables of cross section area 6x1x95+1x70 mm2( 1 hole per phase )
|  | 48-Test pressure of oil leak test of tank | To be filled in
|  | 49-Noise level at 0.3 m distance | To be filled in
50-Transformer oil
|  | A-Type of oil | IEC60296 class 1
|  | B-Manufacturer | To be filled in
|  | C-Place of manufacture | To be filled in
|  | D-Manufactruer’s type designation | To be filled in
|  | E-Applied IEC standard | IEC 60296
|  | F-Kinematic viscosity mm2/s: | To be filled in
|  | At 40 deg | ≤ 16.5
|  | At -15 deg | ≤ 800
|  | G-Flash point | ≥ 140 C
|  | H-Pour point | ≤ - 30 C
|  | I-Density at 20 deg C – kg/dm3 | ≤ 0.895
|  | J-Breakdown strength | kV
|  | K-Dielectric dissipation factor | To be filled in
|  | 51-Dimensions of transformer | L 1230 ( mm) x W 700.(mm) x H 1300.(mm)
|  | 52-54Weight of transformer | kg
53-Type of corrosion protection on steel parts
|  | a) Inside tank | Oil resistant paint
|  | b) Outside tank | Metalized, aluminium paint or equivalent
54-11 kV bushings
|  | A-Name of manufacturer | To be filled in
|  | B-Make/Brand/Model: | To be filled in
|  | C-Reference standard | IEC 60137
|  | D-Type of bushing | To be filled in
|  | E-Rated current | A
|  | F-Rated voltage | KV
|  | G-Material | Porcelain
|  | H-Color | Brown
|  | I-Creepage distance | To be filled in
55-L V bushings
|  | A-Name of manufacturer | To be filled in
|  | B-Make/Brand/Model: | To be filled in
|  | C-Reference standard | IEC 60137
|  | D-Type of bushing | To be filled in
|  | E-Rated current | A
|  | F-Rated voltage | KV
|  | G-Material | Porcelain
|  | H-Color | Brown
|  | I-Creepage distance | To be filled in
|  | 56-Warranty period | One year
|  | 57-Submit Manufacturer certification: | Yes/Required
|  | 58-Submit type test certificates or reports : | Yes/Required
|  | 59-Submit Detail drawings, brochures and catalogues: | Yes/Required