## Annex A.1 Technical Lot 1
Lot 1: Telafar city-Al Kifah neighborhood
| TECHNICAL SPECIFICATIONS AND BILL OF QUANTITIES |  |  | ITB: Reference Number: ITB#03MOS21 -Tel afer district-AL Kifah neighborhood
DRC to complete |  |  |  |  | Bidder to complete |  |  | photos for reference
| Item/Milestone Required | Delivery Location | Unit | Quantity required | Item/Milestone offered (name make and model with full specification) | Country of Origin | Brand | Pictures
Brief Description: replacement of damaged water network for Al Kifah Neighborhood (GPS: Start point (A) 36.485056 42.423046, End point (B) 36.485720 42.416244).
1 | Water Test: The implementing contractor for the project shall carry out the following laboratory tests before implementing the project and after implementing the project, It must be done in the presence and follow-up of the authorized government DoW and DRC supervising engineer, the tests must be done in a government laboratory. -Physical tests. -Chemical tests. -Bacteriological tests. | Telafar district center | LS | 1
2 | Excavation works: Provide materials, machinery and manpower to excavate in the streets and where required, cut in any kind of soil, rock, concrete, or asphalt; with dimensions of (0.7 width, 1.2 depth) m, The price to include removal of surplus excavated materials i.e. soil,old pipe, debris, and organic materials to a suitable place outside city limit approved by the DRC engineer. | Telafar district center | M.L. | 1000
3 | Polyethylene pipes: Supply Polyethylene PE100, HDPE pipes to conform to the EN 12201 and ISO 4427 standards special for potable water applications, pipes shall comply with AWWA Specifications C906, all HDPE pipe and fittings shall be from a single manufacturer, the pipes should comply with the following standards and specifications. - HDPE DN160, PN10, SDR17. - Color: black with blue coextruded stripes. - Thickness to conform with ASTM F714 or ASTM D3035. - stress regression testing in accordance with ASTM D2837. - Material as per ASTM D3350, ASTM D1238. - Weight: not less than 4.50 Kg/m. | Telafar district center | M.L. | 500
4 | Polyethylene pipes: Supply Polyethylene PE100, HDPE pipes to conform to the EN 12201 and ISO 4427 standards special for potable water applications, pipes shall comply with AWWA Specifications C906, all HDPE pipe and fittings shall be from a single manufacturer, the pipes should comply with the following standards and specifications. - HDPE DN110, PN10, SDR17. - Color: black with blue coextruded stripes. - Thickness to conform with ASTM F714 or ASTM D3035. - stress regression testing in accordance with ASTM D2837. - Material as per ASTM D3350, ASTM D1238. - Weight: not less than 2.15 Kg/m. | Telafar district center | M.L. | 500
5 | Installation of PE pipes: Provide materials, machinery and manpower to install the PE pipe line from point A to point B. - The HDPE pipe shall be installed in accordance with the instruction of the manufacturer using Electrofusion (EF) method in accordance to ASTM D2657 and conform to the fitting barcode and specification for field joining of PE pipes - Mechanical connections of the polyethylene pipe to auxiliary equipment such as valves, pumps and tanks shall be through stainless steel bolted flange connections. - All HDPE mains shall be field-tested and the contractor shall supply all manpower, equipment, material, gauges, pumps, meters and incidentals required for testing. Each main shall be pressure tested upon completion of the pipe laying and backfilling operations, including placement of any required temporary roadway surfacing. | Telafar district center | M.L. | 1000
6 | Polyethylene Electrofusion Coupler: Supply PE100, electrofusion coupler to conform to the EN 12201 and ISO 4427 standards special for potable water applications, the coupler shall comply with AWWA Specifications C906, all HDPE pipe and fittings shall be from a single manufacturer, the couplers should comply with the following standards and specifications, 1- HDPE 160 mm, SDR 11, PN16, to conform with ISO S5. 2- Color: black. 3- Limited path fusion indicators. 4- stress regression testing in accordance with ASTM D2837. 5- Material as per ASTM D3350, ASTM D1238. | Telafar district center | No. | 39
7 | Polyethylene Electrofusion Coupler: Supply PE100, electrofusion coupler to conform to the EN 12201 and ISO 4427 standards special for potable water applications, the coupler shall comply with AWWA Specifications C906, all HDPE pipe and fittings shall be from a single manufacturer, the couplers should comply with the following standards and specifications. 1- HDPE 110 mm, SDR 11, PN16, to conform with ISO S5. 2- Color: black. 3- Limited path fusion indicators. 4- stress regression testing in accordance with ASTM D2837. 5- Material as per ASTM D3350, ASTM D1238. | Telafar district center | No. | 39
8 | Bedding and Backfilling: Provide material, machinery and manpower to bed and backfill the excavation path in accordance with the following specification: - Bedding: Using fine sand of at least 0.2 m. - Backfilling: Using fine sand of at least 0.2 m from the pipe top side and around the pipe and clean soil and last layer sub-base at least 15 cm thickness with good compaction not less than 95% . | Telafar district center | M.L. | 1000
9 | PE pipe Lab. Test: Samples of the supplied pipe and fittings shall be tested physically and chemically at a certified construction laboratories prior to the installation. | Telafar district center | No. | 2
10 | Tee 90°, 250/160: Supply and install a Polyethylene Tee 90° 250/160 to conform to the ISO S5 standards special for potable water applications, and shall comply with AWWA specifications C906, all HDPE fittings shall be from a single manufacturer, and the shall comply with the following standards and specifications. - DN: 250. - dn1: 160. - PN10, SDR17, according to ISO S5. | Telafar district center | No. | 1
11 | Reducing 160/110: Supply and install a Polyethylene PE100 to conform to the EN 12201 and ISO 4427 standards special for potable water applications, and shall comply with AWWA specifications C906, all HDPE fittings shall be from a single manufacturer, and the shall comply with the following standards and specifications. - DN: 160. - dn1: 110. - PN10, SDR17. | Telafar district center | No. | 1
12 | Gate Valve DN160, PN10: Supply and install a Resilient-seated gate type valve with bolted cover connection and flanges according to the ANSI/AWWA standard. Design in accordance to ISO 9001:2008, ISO 14001:2004, OHSAS 18001:2007, the supplied valve should be CE marked, the design of the valve should comply to the following standards and specifications, 1- DN160, PN10. 2- Resilient seated in accordance with EN 1074. 3- With flange ends on both sides acc. to ANSI B16.1 Class 125/150. 4- Low operating torque due to plastic sliding guides on the wedge. 5- Equipped with triple O-ring sealing. 6- Body and bonne shall be ductile iron EN-GJS-400-15 (GGG-40). 7- Wedge: Ductile iron EN-GJS-400-15 (GGG-40) encapsulated with EPDM vulcanized. 8- Stem: Stainless steel 1.4021. 9- Stem nut: Brass. 10- Bonnet bolts: Stainless steel A2 (DIN EN ISO 3506). 11- Internally and externally epoxy coated acc. to GSK guidelines. The price also includes installation with all other necessaries ( stainless steel bolts, rubber seal, flanges...etc.) according to the instruction of DRC engineer. | Telafar district center | No. | 1
13 | Elbow L 90°: Supply and install a Polyethylene PE100 L 90° to conform to the EN 12201 and ISO 4427 standards special for potable water applications, and shall comply with AWWA specifications C906, all HDPE fittings shall be from a single manufacturer, and the shall comply with the following standards and specifications. - DN: 160. - PN10, SDR17. | Telafar district center | No. | 4
14 | Household Tapping connections:- connection for housholds: Provide and install of Saddle Compression 160mm with 3/4" PPR pipe, 20bar,120 cm length to connect the household to the main pipe line, the cost not include connecting with the supply pipe of houses. - PPr pipe: Size 3/4", Pressure 20 bars, Operating temperature -20C to 90C. - Application: drinking water. - Fittings: elbow, connector, female elbow, male elbow, tee...etc. to ensure connection to household entrance. | Telafar district center | No. | 200
15 | Electrofusion Stub End: Supply and install a Polyethylene PE100 ° to conform to the EN 12201 and ISO 4427 standards special for potable water applications, and shall comply with AWWA specifications C906, all HDPE fittings shall be from a single manufacturer, and the shall comply with the following standards and specifications, - Material: HDPE110. - DN:110. - PN10, SDR17. | Telafar district center | No | 1
16 | covering PE pipe:- Providing steel pipe (carbon steel ) diameter 10'', to cover PE pipe above the valley to protection from the weather in the point (36.37755 42.422928) and use 10-inch diameter as check point for each gate valve., 1.3 meters long, perpendicular to the valve, fixed by pouring C15 concrete around the pipe. with( 60 * 60 cm) Dimensions along the pipe length and covered by heavy manhole cover, with all work requirements according to the supervising engineer instructions | Telafar district center | M.L | 12
| DRC to complete |  |  |  | Bidder to complete
| Delivery time required (days after PO signature): |  | 30 days |  | Delivery time offered (days after PO signature):
| Delivery Terms required (Add Incoterm if necessary): |  | DDP |  | Delivery Terms offered (must include incoterm):
| Delivery Destination required: |  | Tel afer district-AL Kifah neighborhood |  | Delivery Destination offered:
| Minimum bid validity period required: |  | 90 Days |  | Bid validity period offered:
| Additional comments to bidders: |  |  |  | Company Name:
| 1- All the works must be executed in accordance with the Iraqi General Technical Specifications (I.G.T.S.) published by Ministry of Housing and Reconstruction/ Republic of Iraq, the drawings, contract documents and instructions of the Engineer. 2- All the works and materials must be approved by the project manager Engineer. 3- The materials shall be tested and approved by the National Centre of Construction Laboratories (NCCL). 4- the pressure test should be done for network (pipe flushing/ cleaning and a leaks test) once the works are complete. 5- The contractor must employ a permanent resident Engineer to be present at the project site during the execution period. 6- All equipment shall be manufactured within two years of installation date. 7- Please, read all the documents carefully, visit the site, then price it. |  |  |  | Contact Person:
[5 empty] | Address: |  |  | Phone number:
[5 empty] | Email Address: |  |  | Date:
Do you agree on and accept all the requirements under additional comments to bidder?
Signed by a duly authorized company representative:
Title:
Print Name:
Stamp of company
Yes
NO