## Annex A.1 Technical - LOT 2
Lot 2: Ayadiya city-Al Shurta neighborhood
| TECHNICAL SPECIFICATIONS AND BILL OF QUANTITIES |  |  | ITB: Reference Number: ITB#03MOS21 - Telafar district-Ayadiya town-Al Shurta neighborhood
DRC to complete |  |  |  |  | Bidder to complete |  |  | photos for reference
| Item/Milestone Required | Delivery Location | Unit | Quantity required | Item/Milestone offered (name make and model with full specification) | Country of Origin | Brand | Pictures
Brief Description: Extend of water Network in Al Resala neighborhood - Ba'aj district (GPS:- 36.045899, 41.707364).
1 | Water Test: The implementing contractor for the project shall carry out the following laboratory tests before implementing the project and after implementing the project, It must be done in the presence and follow-up of the authorized government DoW and DRC supervising engineer, the tests must be done in a government laboratory. -Physical tests. -Chemical tests. -Bacteriological tests. | Ayadiya subdistrict center | LS | 1
2 | Cutting the Concrete and Asphalt:- Provide machinery, material and manpower to cut the pipeline path (Asphalt and Concrete) with width 90 cm using saw-cutting machine on both sides along the excavation path. | Ayadiya subdistrict center | M.L. | 650
3 | Excavation works: Provide materials, machinery and manpower to excavate the pipeline path in the street and sidewalk and where required, cut in any kind of soil, rock, with dimensions of (0.9 width, 1.25 depth) m, The price includes removing the surface concrete of the sidewalk using the Jack-Hummer, removal of surplus excavated materials i.e. soil,old pipe, debris, and organic materials to a suitable place outside city limit approved by the DRC engineer. | Ayadiya subdistrict center | M.L. | 650
4 | Polyethylene pipes: Supply Polyethylene PE100, HDPE pipes to conform to the EN 12201 and ISO 4427 standards special for potable water applications, pipes shall comply with AWWA Specifications C906, all HDPE pipe and fittings shall be from a single manufacturer, the pipes should comply with the following standards and specifications. - HDPE DN 250, PN10, SDR17 - Color: black with blue coextruded stripes. - Thickness to conform with ASTM F714 or ASTM D3035. - stress regression testing in accordance with ASTM D2837. - Material as per ASTM D3350, ASTM D1238. - Weight 10.91kg/m. | Ayadiya subdistrict center | M.L. | 650
5 | Installation of HDPE pipes: .Provide materials, machinery and manpower to install the PE pipe line. - The HDPE pipe shall be installed in accordance with the instruction of the manufacturer using Butt fusion welding in accordance to ASTM D2657 and conform to specification for field joining of PE pipes - All HDPE mains shall be field-tested and the contractor shall supply all manpower, equipment, material, gauges, pumps, meters and incidentals required for testing. Each main shall be pressure tested upon completion of the pipe laying and before backfilling operations, including placement of any required temporary roadway surfacing. | Ayadiya subdistrict center | M.L. | 650
6 | Backfilling works:- Provide material, machinery and manpower to bed and backfill the excavation path in accordance with the following specification: - Bedding: Using fine sand of at least 20 cm. - Backfilling: Using fine sand of at least 20 cm from the pipe top side and around the pipe and clean soil and last layer sub-base at least 15 cm thickness with good compaction not less than 95% . | Ayadiya subdistrict center | M.L. | 650
7 | Casting Concrete 1:2:4 for Sidewalks:- Supply of materials, tools and manpower for casting (15cm ) plain concrete (1:2:4),(W 90 cm) using ordinary portland cement for walkways, The work includes all the requirements such formworks and curing it by water for 3 days and according to specification and instruction of site engineer. | Ayadiya subdistrict center | M.L. | 650
8 | PE pipe Lab. Test- Samples of the supplied pipe and fittings shall be tested physically and chemically at a certified construction laboratories prior to the installation. | Ayadiya subdistrict center | LS | 1
9 | Manhole 1.20*1.20m:- Supply tools and materials to construct concrete brick manhole with dimension 1.2*1.2 m from inside and 1.4 m depth,casting by plain concrete 1:2:4 ratio with a thickness 20 cm width 40 cm for the base, building the walls 20cm thickness by soild concrete block (40*20*15 cm), casting Reinforced concrete cover of 20cm thickness (using steel bar 1/2", two layers 15 cm c/c) with steel cover Jager plate 6mm thickness 40*40 cm, painting with anti rust and oil paint, with frame iron angle 1.5", plastering the wall from inside by using cement sand mortar (1:3) ratio, laying gravel 20 cm thickness inside the manholes with all the works according to the site engineer instructions. | Ayadiya subdistrict center | No. | 12
10 | Connection to existing Pipe 8": supply tools, materials and manpower to conect the new pipe 10" to existing pipe 8" the work includes all accessories like (tee 10"/8", flanges, iron coupling 8"…etc). The work should carry out according to specification and instruction of the site engineer. | Ayadiya subdistrict center | No. | 1
11 | Connection to existing Pipe 6": supply tools, materials and manpower to conect the new pipe 10" to existing pipe 6" the work includes all accessories like (tee 10"/6", flanges, iron coupling 6"…etc). The work should carry out according to specification and instruction of the site engineer | Ayadiya subdistrict center | No. | 4
12 | Connection to existing Pipe 4": supply tools, materials and manpower to conect the new pipe 10" to existing pipe 4" the work includes all accessories like (tee 10"/4", flanges, iron coupling 4"…etc). The work should carry out according to specification and instruction of the site engineer | Ayadiya subdistrict center | No. | 2
13 | Gate Valve DN250, PN10: Supply and install a Resilient-seated gate type valve with bolted cover connection and flanges according to the ANSI/AWWA standard. Design in accordance to ISO 9001:2008, ISO 14001:2004, OHSAS 18001:2007, the supplied valve should be CE marked, the design of the valve should comply to the following standards and specifications, 1- DN 250, PN10. 2- Resilient seated in accordance with EN 1074. 3- With flange ends on both sides acc. to ANSI B16.1 Class 125/150. 4- Low operating torque due to plastic sliding guides on the wedge. 5- Equipped with triple O-ring sealing. 6- Body and bonne shall be ductile iron EN-GJS-400-15 (GGG-40). 7- Wedge: Ductile iron EN-GJS-400-15 (GGG-40) encapsulated with EPDM vulcanized. 8- Stem: Stainless steel 1.4021. 9- Stem nut: Brass. 10- Bonnet bolts: Stainless steel A2 (DIN EN ISO 3506). 11- Internally and externally epoxy coated acc. to GSK guidelines. The price also includes installation with all other necessaries ( stainless steel bolts, rubber seal, flanges...etc.) according to the instruction of DRC engineer. | Ayadiya subdistrict center |  | 5
14 | Gate Valve DN160 (6"), PN10: Supply and install a Resilient-seated gate type valve with bolted cover connection and flanges according to the ANSI/AWWA standard. Design in accordance to ISO 9001:2008, ISO 14001:2004, OHSAS 18001:2007, the supplied valve should be CE marked, the design of the valve should comply to the following standards and specifications, or equivalent as approved by the DRC Engineer: 1- DN160 (6"), PN10. 2- Resilient seated in accordance with EN 1074. 3- With flange ends on both sides acc. to ANSI B16.1 Class 125/150. 4- Low operating torque due to plastic sliding guides on the wedge. 5- Equipped with triple O-ring sealing. 6- Body and bonne shall be ductile iron EN-GJS-400-15 (GGG-40). 7- Wedge: Ductile iron EN-GJS-400-15 (GGG-40) encapsulated with EPDM vulcanized. 8- Stem: Stainless steel 1.4021. 9- Stem nut: Brass. 10- Bonnet bolts: Stainless steel A2 (DIN EN ISO 3506). 11- Internally and externally epoxy coated acc. to GSK guidelines. The price also includes installation with all other necessaries ( stainless steel bolts, rubber seal, flanges...etc.) according to the instruction of DRC engineer. | Ayadiya subdistrict center |  | 4
15 | Gate Valve DN110 (4"), PN10: Supply and install a Resilient-seated gate type valve with bolted cover connection and flanges according to the ANSI/AWWA standard. Design in accordance to ISO 9001:2008, ISO 14001:2004, OHSAS 18001:2007, the supplied valve should be CE marked, the design of the valve should comply to the following standards and specifications, 1- DN110 (4"), PN10. 2- Resilient seated in accordance with EN 1074. 3- With flange ends on both sides acc. to ANSI B16.1 Class 125/150. 4- Low operating torque due to plastic sliding guides on the wedge. 5- Equipped with triple O-ring sealing. 6- Body and bonne shall be ductile iron EN-GJS-400-15 (GGG-40). 7- Wedge: Ductile iron EN-GJS-400-15 (GGG-40) encapsulated with EPDM vulcanized. 8- Stem: Stainless steel 1.4021. 9- Stem nut: Brass. 10- Bonnet bolts: Stainless steel A2 (DIN EN ISO 3506). 11- Internally and externally epoxy coated acc. to GSK guidelines. The price also includes installation with all other necessaries ( stainless steel bolts, rubber seal, flanges...etc.) according to the instruction of DRC engineer | Ayadiya subdistrict center |  | 2
| DRC to complete |  |  |  | Bidder to complete
| Delivery time required (days after PO signature): |  | 30 days |  | Delivery time offered (days after PO signature):
| Delivery Terms required (Add Incoterm if necessary): |  | DDP |  | Delivery Terms offered (must include incoterm):
| Delivery Destination required: |  | Telafar district-Ayadiya town-Al Shurta neighborhood |  | Delivery Destination offered:
| Minimum bid validity period required: |  | 90 Days |  | Bid validity period offered:
| Additional comments to bidders: |  |  |  | Company Name:
| 1- All the works must be executed in accordance with the Iraqi General Technical Specifications (I.G.T.S.) published by Ministry of Housing and Reconstruction/ Republic of Iraq, the drawings, contract documents and instructions of the Engineer. 2- All the works and materials must be approved by the project manager Engineer. 3- The materials shall be tested and approved by the National Centre of Construction Laboratories (NCCL). 4- the pressure test should be done for network (pipe flushing/ cleaning and a leaks test) once the works are complete. 5- The contractor must employ a permanent resident Engineer to be present at the project site during the execution period. 6- All equipment shall be manufactured within two years of installation date. 7- Please, read all the documents carefully, visit the site, then price it. |  |  |  | Contact Person:
[5 empty] | Address: |  |  | Phone number:
[5 empty] | Email Address: |  |  | Date:
Do you agree on and accept all the requirements under additional comments to bidder?
Signed by a duly authorized company representative:
Title:
Print Name:
Stamp of company
Yes
NO