## BoQ - UPVC pipe line-Qatoon
Annex A 1-Technical Bid Form
Extension of Storm water Sewer UPVC Pipeline(540m) near Beirut office in Qatoon-Baqubah District مد انابيب مجاري مياه الامطار (540 م) قرب مكتب بيروت في الكاطون - قضاء بعقوبة
Project Location
Governorate |  | Diyala | Sub-district |  | Baqubah |  | GPS Coordinates
District |  | Baqubah | Town/Village |  | Qatoon |  | 33.738 | 44.598
All material must be heavy-duty type. All supplied accessories and materials require sampling provision prior acceptance by the supervising engineer. All structural concrete work must be according to ACI 318M-2014 code, and all work must be according to the Iraqi Technical standards, and DRC’s engineer instructions.
Item | Description |  |  |  | Unit | Qty | Description | Origin made
1 | UPVC Pipes with Excavation and backfill Works: Supply, excavate, extend, burying, test, connect and operate UPVC pipeline pressure of (6 bar) with rubber attachments successful in laboratory tests (DIN 8061 & 8062) and the materials needed to implement sewer lines. The price includes the transportation of pipes, drilling the line with extend and pressing the pipes with supply sand-gravel mixture class (B) supported by its success in a laboratory to covered the pipe from all directions thickness (30) cm with good compaction by using a small mechanical compacting machines under the pipe and to a level of 60 cm above the pipe with pull of groundwater according to requirement of the site. The line should be free of water with cleaning the pipe from mud sediments in addition to backfill (bury) the path of the line with a layers of clean soil (25 cm thickness for each layer) with good compaction by using mechanical compacting machines to the level of ground with ratio 95% that match laboratory test, settlement the site and return street to what it was, according to the road specifications and general standard specifications of sewer (DoS), the price includes all necessary laboratory tests and wages of street cracking by using (Cutter machine). The path of the excavation line must be surveyed and reflected to (GIS) and according to instruction of supervisor engineer. |  |  | أنابيب UPVC مع اعمال الحفر والدفن: تجهيز وحفر ومد ودفن وفحص وربط وتشغيل انابيب بلاستك UPVC ضغط (6 جو)، مع الملحقات المطاطية على ان يكون ناجح في الفحوصات المختبرية (DIN 8061 & 8062) والمواد اللازمة لتنفيذ خطوط المجاري, ويشمل السعر أجور نقل الانابيب مع حفر الخط مع مد وكبس الانابيب مع تجهيز حصى خابط صنف (B) مؤيدة بنجاحه مختبريا لتغليف الانبوب من جميع الجهات وبسمك 30سم مع حدلها جيدا بواسطة الحادلات الميكانيكية الصغيرة تحت الانبوب والى مستوى 60 سم فوق الانبوب مع سحب المياه الجوفية حسب متطلبات موقع العمل على ان يكون مسار الحفر خالي من المياه مع تنظيف الانبوب من الترسبات الطينية بالاضافة الى اعادة دفن مسار الخط بالتراب النظيف وبطبقات وبسمك 25 سم للطبقة الواحدة مع الحدل الجيد باستخدام الحادلات الميكانيكية الى مستوى الارض وبنسبة 95 % مؤيدة للفحوصات المختبرية مع تسوية الموقع واعادة الشارع على ما كان عليه بموجب مواصفات الطرق ويكون العمل بموجب المواصفات القياسية العامة للمجاري, ويشمل السعر اجور كافة الفحوصات المختبرية اللازمة واجور تكسير الشارع باستخدام الكتر ,مع تثبيت الخطوط بنظام (GIS) وحسب توجيهات المهندس المشرف.
| 1- Supply UPVC sewer pipe line (6 bar) ,315mm diameter, 6-m length and average depth (1.5 - 2.5)m. To be purchased and entered into warehouse of DoS. |  |  | 1- تجهيز خطوط مجاري UPVC (6 بار) ، قطر 315 ملم ، طول 6 م و بعمق يتراوح (1.5-2.5) م. على أن يتم شرائها وأدخالها مخزنيا. | M.L | 540
| 2- Supply UPVC sewer pipe line (6 bar) ,200mm diameter, 6-m length and average depth (0.9 - 1.2)m. To be purchased and entered into warehouse of DoS. |  |  | 2- تجهيز خطوط مجاري UPVC (6 بار) ، قطر 200 ملم ، طول 6 م وبعمق يتراوح (0.9-1.2) م. على أن يتم شرائها وأدخالها مخزنيا. | M.L | 275
2 | Main Manholes: Supply materials to be laboratory successful and working to pour the main circular manholes of sewage lines from reinforced concrete resistant to salts with a mixing ratio of 3: 1.5: 1 (30 MPa), and a thickness of the walls and ceiling 25 cm, thickness of the floor 50 cm, the price includes the costs of laboratory tests, pull groundwater and casting a layer of (blinding) from the usual concrete resistant to salts with a thickness of 10 cm. The work should be using a moisture inhibitor (Flankot) on the outside, and an epoxy with sealant (water stope) on the inside, with fixing the pipe to the ordinary concrete resistant to salts according to the drawings and instructions of the supervisor engineer. |  |  | المنهولات الرئيسية: تجهيز مواد على ان تكون ناجحة مختبريا وعمل لصب المنهولات الرئيسية الدائرية لخطوط المجاري من الخرسانة المسلحة المقاومة للاملاح وبنسبة خلط 3:1.5:1 (30 ميكا باسكال )وبسمك للجدرا ن والسقف 25 سم وبسمك للأرضية 50 سم, ويشمل السعر أجور الفحوصات المختبرية وسحب المياه الجوفية وصبة طبقة (blinding) من الخرسانة الاعتيادية المقاومة للاملاح بسمك 10 سم ويكون العمل باستخدام مانع الرطوبة (الفلانكوت) من الخارج والايبوكسي من الداخل ومانع التسرب (water stope) مع تثبيت الانبوب بالخرسانة العادية المقاوم للاملاح وفق المخططات وتوجيهات المهندس المشرف.
| a- Manhole with internal diameter (1.1)m for sewer line 315mm with average depth 2 m, 14 manhole. |  |  | أ- منهول قطر داخلي (1.1) م لخط المجاري 315 ملم بمعدل عمق 2 م عدد 14 منهول. | No. | 14
| b- Supply, install and fixing the round iron cover with the base (55) cm diameter from heavy duty. (Similar to Turkish origin or equivalent) connected to the frame by a heavy duty hinges. |  |  | ب- تجهيز وتثبيت وتركيب الغطاء الحديدي المدور مع القاعدة قطر (55) سم من النوع الثقيل (مشابه للمنشأ التركي او ما يماثله) و مربوط بالاطار بواسطة نرمادات من النوع الثقيل | No. | 14
3 | Gully Side (Street Gutters): Supply materials to be successful with laboratory tests and work to pour the side gully of plain concrete resistant to salts with a mixing ratio of 3: 1.5: 1 and thickness of the walls and floors (15) cm, internal dimensions (90x35x25) cm. |  |  | الكليات الجانبية: تجهيز مواد على ان تكون ناجحة بالفحوصات المختبرية وعمل لصب الكليات الجانبية من الخرسانة الغير مسلحة المقاومة للاملاح وبنسبة خلط 3:1.5:1 وسمك للجدران والارضية (15) سم وبأبعاد داخلية (90x35x25) سم. | No. | 28
4 | Steel Cover-Grid Supply, install and fixing steel of grid cover with the base and dimensions (38x28) cm of heavy duty type. |  |  | المشبك الحديدي تجهيز وتثبيت وتركيب المشبك الحديدي مع القاعدة وبابعاد (38x28) سم من النوع الثقيل. | No. | 28
DRC to complete |  |  |  | Bidder to complete
Delivery time required (days after PO signature): |  | 40 Days |  | Delivery time offered (days after PO signature):
Delivery Terms required (Add Incoterm if necessary): |  | DDP INCOTERMS 2020 |  | Delivery Terms offered (must include incoterm):
Delivery Destination required: |  | Diyala - Mansoria. |  | Delivery Destination offered:
Minimum bid validity period required: |  | 90 Days |  | Bid validity period offfered:
Currency of Tender: |  | USD only |  | Currency of Bid:
Additional Comments: Bidders should note that Delivery will be to DRC Distribution sites. Possible Delivery District Locations have been listed in the "Delivery Destination required" cell. Prices should include Delivery to the various locations. Delivery may be requested in required quantities to several locations simultaneously. |  |  |  | Company Name:
Signed by a duly authorized company representative:
Title:
Date:
Print Name:
Stamp of company
Note on J5: Author: Latitude
Note on K5: Author: Longitude