## LOT 1
ANNEX 1 TECHNICAL SPECIFICATION FOR PUMPS AND MOTORS
Item No. | Description | Unit | Quantity
LOT 1: Supply of Submersible Pumps
1 | supplying steel submersible pump for pumping non-aggressive portable water without solid particles from a borehole, water temoerature from 15 to 45 degrees Celduis with all needed accessories and a discharge base 3*380 volt 50Hz of :H=214m Q=8 m3/h. the pump and motor should be matching the following specifications: Pump (directly coupled to an electric motor and fitted with AISI 304 stainless steel body and shaft, impeller/diffuser assemblies made from AISI 304 stainless steel or Noril glass fibre impregnated thermoplastic resin, water-lubricated rubber bearings, top non-return valve, bottom strainer, female outlet threaded as per ISO 65, tail electric cable. Efficiency (minimum) 65% for 4" to 5" pumps, 70% for 6" to 7" pumps, 75% for 8" pumps and above. Motor, 3-phase electric motor, suitable for power supply of 380 V (+/- 5%), 50 Hz (+/- 5%), 3 ph, asynchronous squirrel cage motor, canned type, with slide bearings, motor made of stainless steel AISI 304, shaft made of stainless steel AISI 304, enclosure class IP 58, water lubicated bearings, including one built in temperature sensor. Motor overload margin over the rated pump power: 1.10 times. Hermetically sealed resin encased stators. | pieces | 1
2 | same upper submersible pump but with H= 130 m Q= 17 m3/h | pieces | 3
3 | same upper submersible pump but with H=160m Q=17 m3/h | pieces | 2
4 | same upper submersible pump but with H=205m Q=17 m3/h | pieces | 2
5 | same upper submersible pump but with H=329m Q=17 m3/h | pieces | 1
6 | same upper submersible pump but with H=110m Q=30 m3/h | pieces | 3
7 | same upper submersible pump but with H=155m Q=30 m3/h | pieces | 3
8 | same upper submersible pump but with H=194m Q=30 m3/h | pieces | 3
9 | same upper submersible pump but with H=233m Q=30 m3/h | pieces | 2
10 | same upper submersible pump but with H=272m Q=30 m3/h | pieces | 5
11 | same upper submersible pump but with H=160m Q=7 m3/h | pieces | 2
12 | same upper submersible pump but with H=140m Q=5 m3/h | pieces | 2
13 | same upper submersible pump but with H=150m Q=15 m3/h | pieces | 3
14 | same upper submersible pump but with H=180m Q=20 m3/h | pieces | 2
15 | same upper submersible pump but with H=100m Q=20 m3/h | pieces | 3
16 | same upper submersible pump but with (H=170m Q=30 m3/h | pieces | 3
17 | same upper submersible pump but with H=110m Q=30 m3/h | pieces | 2
18 | Intake submersible pump: Supplying a Surface water intake submersible pump the pumps should be for river raw water, with all needed fitting and accessories according to specification of CR 64-7-1 A-F-A-E-HQQE, Pump orientation: Vertical. Shaft seal arrangement: Single Curve tolerance: ISO9906:2012 3B Materials Base: Cast iron, EN 1563 EN-GJS-500-7, ASTM A536 80-55-06 Impeller: Stainless steel, EN 1.4301, AISI 304 Bearing: SIC Support bearing: Graflon Installation Maximum ambient temperature: 55 °C Maximum operating pressure: 30 bar Max pressure at stated temp: 30 bar / 120 °C 30 bar / -30 °C Type of connection: DIN Size of inlet connection: DN 100 Size of outlet connection: DN 100 Pressure rating for connection: PN 40 Flange size for motor: FF350 Liquid temperature range: -30 .. 120 °C Density: 998.2 kg/m³ Electrical data Motor standard: IEC 34-5) IP 55 IE Efficiency class: IE3 Rated power : (P2 ) 37 kW Power (P2) required by pump: 37 kW Mains frequency : 50 Hz Rated voltage: 3 x 380-420D/660-725Y V Rated current: 68,0-63,0/39,0-36,0 A Requested voltage: 400 V Rated current at this voltage: 65.5 A Starting current: 670-670 % Cos phi - power factor: 0.88 Rated speed: 2955 rpm Efficiency: IE3 93,7% Motor efficiency at full load: 93.7-93.7 % Motor efficiency at 3/4 load: 93.9-93.9 % Motor efficiency at 1/2 load: 93.5-93.5 % Number of poles: 2 Enclosure class: (IEC 34-5) IP55 Insulation class: (IEC 85) F Motor protect: PTC Controls Minimum efficiency index: MEI ≥0.70 Net weight: 354 kg Gross weight: 398 kg Shipping volume: 0.808 m³ | pieces | 4
B. Delivery
All Items should Be delivered to Water directorate warehouse /Iraq/ Duhok
C. Remarks And Condition
1 | Certification of origin for all offered items should be provided before delivery.
2 | Submit Manufacturer certification and test reports for all offered items should be provided before delivery.
3 | Catalogues (should be European Brand or equivalent Brand) and tech. specifications with datasheets should be provided with offers .

## LOT 2
ANNEX 1 TECHNICAL SPECIFICATION FOR PUMPS AND MOTORS
Item No. | Description | Unit | Quantity
LOT 2: Supply of Submersible Motors and Accessories
1 | Submersible motor 5.5 KW(west European made) with socket and compound joint paste (works with temp. arrive50 deg. C.).borehole (8)" | pieces | 2
2 | Submersible motor 7.5 KW (west European made) with socket and compound joint paste (works with temp. arrive50 deg. C.).borehole (8)" | pieces | 3
3 | Submersible motor 11 KW (west European made) with socket and compound joint paste (works with temp. arrive50 deg. C.).borehole (8)" | pieces | 3
4 | Submursible motor 11KW (Riwindable motors) West European made with socket and compound joint paste (works at temp. arrive deg. C.) | pieces | 2
5 | Submersible motor 15 KW (west European made) with socket and compound joint paste (works with temp. arrive50 deg. C.).borehole (8)" | pieces | 4
6 | Submersible motor 18.5 KW (west European made) with socket and compound joint paste (works with temp. arrive50 deg. C.).borehole (8) | pieces | 4
7 | Submursible motor 18.5KW (Riwindable motors) West European made with socket and compound joint paste (works with temp. arrive deg. C.) | pieces | 2
8 | Submersible motor 22 KW (west European made) with socket and compound joint paste (works with temp. arrive 50deg. C.).borehole (8)" | pieces | 4
9 | Submersible motor 30 KW (west European made) with socket and compound joint paste (works with temp. arrive 50deg. C.).borehole (8)" | pieces | 4
10 | Submersible motor 45 KW (west European made) with socket and compound joint paste (works with temp. arrive50 deg. C.) | pieces | 1
11 | Submersible motor 37 KW (west European made) with socket and compound joint paste (works with temp. arrive50 deg. C.) | pieces | 1
12 | supply an electrical squirrel cage motor (horizontal) 132 kw of a speed (1500) rpm 4poles. And suitable ±10% volts, 3- phase, 50 Hz ±5%. | pieces | 1
13 | supply an electrical squirrel cage motor (horizontal) 75 kw of a speed (1500) rpm 4poles. And suitable ±10% volts, 3- phase, 50 Hz ±5%. | pieces | 1
14 | supply an electrical squirrel cage motor (horizontal) 37 kw of a speed (1500) rpm 4poles. And suitable ±10% volts, 3- phase, 50 Hz ±5%. | pieces | 1
15 | supply electrical control panel auto transformer type of (11 KW . 400V .50 H2) three phase including the following protective means: (main circute breaker . main fuzes phase, sequeence protective relay, overload relay, High, low vollage cut off . Voltmeter and ammeter . Coil contactor ( 380 V). Specifications of control panel and starter: one enclosure IP 55 to IEC 529 with door and key, one start door mounted pushbutton, one stop reset door mounted pushbutton, one selector switch Manual-Off-Automatic, one four pole TNP contactor (triple pole and neutral), one DOL starter for power consumption at start up less than 5.5 kW or one auto-transformen for power consumption at start-up exceeding 5.5 kW to IEC 947, cotrol lights: Run / stop, one current converter including provision for ampere setting, door mounted ampere display, one voltmeter with changeover switch, one phase failure relay, one overload relay for current protection. | pieces | 4
16 | supply electrical control panel of same specifications as item 47 But of 5.5 KW .electric capability | pieces | 1
17 | supply electrical control panel of same specifications as item 47 But of 7.5 KW .electric capability | pieces | 3
18 | supply electrical control panel of same specifications as item 47 But of 15 KW .electric capability | pieces | 5
19 | supply electrical control panel of same specifications as item 47 But of 18.5 KW .electric capability | pieces | 4
20 | supply electrical control panel of same specifications as item 47 But of 22 KW .electric capability | pieces | 5
21 | supply electrical control panel of same specifications as item 47 But of 30 KW .electric capability | pieces | 5
22 | supply electrical control panel of same specifications as item 47 But of 37 KW .electric capability | pieces | 1
23 | supply electrical control panel of same specifications as item 47 But of 45 KW .electric capability | pieces | 1
24 | supply Galvanized pipes with screw -threaded ends ( 2.5" diameter 6m length . weight 41.5 kg) threaded from both sides equiped with pipe coupling cover from the other side | pieces | 150
25 | supply Galvanized from pipes with screw -threaded ends ( 3" diameter 6m length . weight 54.4kg) threaded from both sides equiped with pipe coupling cover from the other side | pieces | 170
26 | supply Galvanized from pipes with screw -threaded ends ( 4" diameter 6m length . weight 78kg) threaded from both sides equiped with pipe coupling cover from the other side | pieces | 120
27 | Flexible cable insulation from rubber heavy duty temp. rating (-25C upto 60C) wire made of copper (3*6)mm. Type ( HO7RN-F) Best quality | m.l | 200
28 | Flexible cable insulation from rubber heavy duty temp.rating (-25C upto 60C) wire made of copper (3*10)mm. Type( HO7RN-F) Best quality | m.l | 450
29 | Flexible cable insulation from rubber heavy duty temp .rating (-25C upto 60C) wire made of copper (3*16)mm. Type( HO7RN-F) Best quality | m.l | 450
30 | Flexible cable insulation from rubber heavy duty temp. rating (-25C upto 60C) wire made of copper (3*25)mm. Type ( HO7RN-F) Best quality | m.l | 150
B. Delivery
All Items should Be delivered to Water directorate warehouse /Iraq/ Duhok
C. Remarks And Condition
1 | Certification of origin for all offered items should be provided before delivery.
2 | Submit Manufacturer certification and test reports for all offered items should be provided before delivery.
3 | Catalogues (should be European Brand or equivalent Brand) and tech. specifications with datasheets should be provided with offers .

## LOT 3
ANNEX 1 TECHNICAL SPECIFICATION FOR PUMPS AND MOTORS
Item No. | Description | Unit | Quantity
LOT 3: Supply of Horizontal Pumps
1 | Horizontal Pumps: Supplying a horizontal axis, radially split, ring section design, multistage centrifugal pump of non-self priming type Pump. The Pump and motor should be fitted on a common base plate and connected to each other via flexible coupling. The pump should be according to the specification of OMK 65, 1450. Flanges should be acc. to DIN 2535. Flanges acc. to BS or ANSI should be upon request. Chromium steel (AISI 420) fine grained shafts should be used on the pumps. Discharge part should be at motor side on top, suction part should be at dead end side on the right and rotation of direction is clockwise when viewed from driver. Suction and discharge nozzles should be a choice of three 90° positions. By special request, should be possible to put the suction nozzle at the motor side. In this arrangement pump and motor rotation must be counter clockwise. On both ends, bearing houses should be equipped with grease lubricated heavy duty ball bearings. Bearing at the suction side should be fixed. Extra axial load should be carried by this bearing. Shaft Seal should be Uncooled gland packing should be (Up to 110 °C). Standardized, single acting, balanced and uncooled mechanical seal should be (Up to 140 °C). Double-acting and cartridge seals should be upon request. Discharge side bearing is free at the axial direction and it carries only radial load. Throwers and lip seals should be on the shaft to prevent leakage fluid from getting into bracket. Suction Flange: DN 50…DN 125 (PN 40) (DIN2535) Discharge Flange: DN 32…DN 80 (PN 40) (DIN 2535) Operating Pressure: 40 Bar Stage Number: 2 - 14 Flow Range: 65 m³/h Head Range: 160 m Temperature Range: 10 - 140 °C; mechanical seal Max Speed : -10 - 110 °C; soft packing RPM: 1500 rpm | pieces | 4
B. Delivery
All Items should Be delivered to Water directorate warehouse /Iraq/ Duhok
C. Remarks And Condition
1 | Certification of origin for all offered items should be provided before delivery.
2 | Submit Manufacturer certification and test reports for all offered items should be provided before delivery.
3 | Catalogues (should be European Brand or equivalent Brand) and tech. specifications with datasheets should be provided with offers .