## LOT 1 -Generator 200 KVA
LOT 1 - SUPPLY AND INSTALLATION OF 200 kVA, 160ekW GENERATORS
POS. | TECHNICAL SPECIFICATIONS | COMPARATIVE SPECIFICATION / REMARKS
| Minimum technical requirements. | Comparative specification / remarks should indicate any deviation from technical parameter or functional description of tender specification or confirmation with "Yes" and if applicable further particularities.
1.0 | Diesel Generating Set with synchronization control system, water cooled, incl. sound and water proofed canopy; Stationary version, incl. lifting hook; tropicalized, ready for use, fitted as complete unit on a rigid base frame (e.g. skid mounted/concrete slab), consisting of Motor, Alternator, Battery, Fuel tank and separate switch board and accessories mentioned below. Norms and reference values to be followed: VDE, EN, DIN, ISO or equivalent norms. In particular VDE 0100 Teil 551/560, VDE 0108, DIN ISO 8528, DIN ISO 3046 and/or norms or other guidelines as may be menitoned in the present specification.
1.0.1 | Prime Power: 200 kVA (Tolerance + 10 / - 0 KVA) taking into consideration the environmental conditions (variable continuous output PRP per DIN ISO 8528)
1.0.2 | Please indicate:
1.0.3 | Variable continuous output PRP per DIN ISO 8528 by standard test conditions
1.0.4 | Variable continuous PRP per DIN ISO 8528 in reference to the environmental conditions
1.0.5 | Overall efficiency
1.0.6 | Type of Power Generator (Manufacturer, Brand, Model, Type)
1.0.7 | Site of operation / Purpose / Environmental conditions Outdoor installation in Iraq minimum -10°C and maximum up to +55°C, Altitude Up to 1000 meters above sea-level, Average Air humidity yearly minimum 12%, average 45 %, maximum 92%.
1.0.8 | CE declaration of conformity by the manufacturer exists. Please attach the document to your offer.
CE compliance of Generator, Motor and Alternator. Products/ Parts are labelled.
1.1 | Composition of unit
1.1.1 | Welded sectional steel base frame , warp resistant, lifting hook on each corner for easy lifting
1.2
1.2.1 | MOTOR, Norms and reference values: ISO 3046, DIN 6271, BS 5514 or equivalent international standards
1.2.2 | Type: Diesel, direct injection, forced oil lubrication, fuel transfer pump
1.2.3 | Revs : 1500 rpm
1.2.4 | Speed regulation : Mechanical/Electronic
1.2.5 | Cooling: water cooled, considering a surrounding temperature of 40°C
1.2.6 | Built-in Fuel Tank: steel, fitted to the frame, incl. fuel level gauge. Tank capacity: at least for a 8 hours run under maximum continuous output.
Please indicate:
1.2.7 | Motor brand and designation, Model and Type
1.2.8 | Number of cylinders and cubic capacity
1.2.9 | Fuel tank capacity
1.2.10 | Oil capacity
1.2.11 | Motor capacity as per ISO 3046-7 based on 25°C intake temperature, 25°C cooling water intake temperature, 1.000 mbar air pressure, 30% air humidity – (KW)
1.2.12 | Motor capacity as per ISO 3046 in reference of the environmental conditions, mechanical (KWm)
1.2.13 | Motor capacity as per ISO 3046 in reference to the environmental conditions, electrical (KWe)
1.2.14 | Motor efficiency
1.2.15 | Fuel consumption as per ISO 3046-1 including attached pumps.
1.2.16 | Diesel consumption below 50 H/hr at 100% load
1.2.17 | Diesel consumption below 38 H/hr at 75% load
1.2.18 | Diesel consumption below 26 H/hr at 50% load
1.2.19 | Lubrication oil consumption (ltr/h) under standard conditions
1.3 | ALTERNATOR Norms and reference values: VDE 0530, BS 4999, UTE NFnC 51.111, IEC 34.1, NEMA MG 21
1.3.1 | Three-phase current alternator as per VDE 0530, internal pol machine with damping winding, self-regulating, self-starting
1.3.2 | Voltage rigidity : max 5 %
1.3.3 | Nominal voltage: 230V alternating current, 400V three-phase current
1.3.4 | Frequency: 50 Hz
1.3.5 | Power factor: cos phi 0,8
1.3.6 | Insulation class: H
1.3.7 | Isolation good for tropic climate
1.3.8 | Radio interference suppression according to VDE 0875 “N”
1.3.9 | Protection class DIN 40050, IP 23
1.3.10 | G3 Classification according to DIN ISO 8528
1.3.11 | The alternator shall be synchronous, four pole and brushless excitation type and shall comply with the relevant requirements of Specification IEC 60034 or an equivalent international standard.
Please indicate:
1.3.11 | Alternator brand, model, type
1.3.12 | Efficiency factor of Alternator
1.4 | Exhaust System, Soundproofing
1.4.1 | Weather and sound proofed canopy incl. exhaust silencer. High corrosion resistance: stainless covered with zinc and made in dichromate. Large doors allow easy access to the generator set for service and monitoring purposes. Lockable doors with one window showing the control panel, fully assembled for immediate use. Exhaust system fully integrated (inner mounted). Emergency stop button is accessible from outside enclosure.
1.4.2 | Acoustic pressure level at 1 m distance below 82 dbA at full continuous load
1.4.3 | Acoustic pressure level at 7 m distance below 70 dbA at full continuous load
1.4.4 | Acoustic pressure level at 10 m distance below 65 dbA at full continuous load
1.5 | Control fittings / Measuring Instruments / Switch board (ATS)
1.5.1 | Switch cabinet - vibration proof – fitted to the steel base frame
1.5.2 | Motor protection accessories (Oil pressure, water temperature, excessive revs) Generator protection switch, thermic-magnetic overload protection, protection of Instruments and indicators
1.5.3 | Battery-charging control light, oil-pressure warning light, excessive-temperature warning light, light test, excessive revs alarm, false start light, emergency-off light, central warning light
1.5.4 | Measuring instruments, switches; 1 x Ampere meter, 1 x Voltmeter with switch, 1 x frequency measuring unit, 1 x operation hours counter, emergency “off” button, manual mode switch
1.5.5 | 50 m reinforced electrical cable for electrical power supply, under- or above ground use
1.5.6 | 5 m yellow-green cable with ground pin
1.5.7 | Labeling of all components in English language
Please indicate:
1.5.8 | Dimensions of one unit: (length x width x height)
1.5.9 | Weight of one unit in kg (without any fillings)
1.6 | DOCUMENTATION
1.6.1 | Manual for installation, commissioning and use plus a spare parts catalogue for each part of the generator (motor, generator, switch board, wiring diagram) in English and if available Arabic language
1.7 | LOCAL AGENCY / AFTER SALES SERVICE Providing Aftersales Service/Support and Maintenance for the proposed generators in Iraq is advantageous.
Please indicate:
1.7.1 | Address of the local agency or agency within the region
1.8 | Spare parts / Maintenance parts / Consumables covering 1.000 hrs of operation
1.8.1 | 2 pc. Oil filters
1.8.2 | 1 pc. Air filter
1.8.3 | 2 pc. Fuel filter ext.
1.8.4 | 1 set of seals, screws, nuts, etc, for 1.000 hrs of operation
1.8.5 | 1 pc. V-belt
1.9 | Standard tool set
1.9.1 | Standard tool set to provide maintenance and small repairs up to 1.000 hrs of Operation
Please indicate:
1.9.2 | Tool set list as per 1.9.1
1.10 | Dimensions / Weights
1.10.1 | Dimensions (length x width x height) without packing
1.10.2 | Dimensions (length x width x height) incl. packing for sea/road transport
1.10.3 | Weight (kg) empty without packing
1.10.4 | Weight (kg) empty incl. packing for sea/road transport
1.11 | Insurance / Conditions
1.11.1 | The cost of transit insurance relating to the items to be transported by the contractor to the site of work shall be borne by the contractor/supplier and the quoted price shall be inclusive of this cost.
1.11.2 | The offered equipment shall be brand new with state of art technology and proven field track record. No prototype equipment shall be offered.
1.12 | Site Installation Condition and Synchronization
1.12.1 | The supplier shall provide and install synchronization control unit for load sharing across both interconnected generators
1.12.2 | The generator set shall be provided with a sound attenuated housing which allows the generator set to operate at full rated load in the ambient conditions. The enclosure shall reduce the sound level of the generator set while operating at full rated load to below 82 dBA at 1 meter from the generator set. Housing configuration and materials used may be of any suitable design which meets application needs, except that acoustic materials used shall be oil and water resistant. No foam materials shall be used.
1.12.3 | The enclosure shall be provided with an exhaust silencer, which is mounted outside of the enclosure, and allows the generator set package to meet specified sound level requirements. Silencer and exhaust shall include a rain cap and rain shield.
1.12.4 | Complete unit to be mounted on robust skid frame. Vibration mountings to be used where required. Skid frame to be dimensioned to accommodate generator/alternator assembly, all accessories, sound proof canopy. Skid frame to be of rigid construction suitable for locating on level ground surface concrete pad. The concrete pad will be provided by GIZ.

## LOT 2 - FUEL TANKS
LOT 2 - SUPPLY AND INSTALLATION OF TWO ABOVE GROUND ATMOSPHERIC FUEL TANKS
POS. | TECHNICAL SPECIFICATIONS | COMPARATIVE SPECIFICATION / REMARKS
| Minimum technical requirements. | Comparative specification / remarks should indicate any deviation from technical parameter or functional description of tender specification or confirmation with "Yes" and if applicable further particularities.
2.0 | External Fuel Tank, Pipe and Fittings
2.0.1 | 2 Nos. of external fuel tanks of 2000 liter capacity shall be provided. Provide pre-engineered aboveground atmospheric tank system complete with tank, piping, secondary containment, gauges, and other accessories specified herein as a complete assembled system including analog fuel meter. The external tank shall have a total volume of 4000 liters to provide the diesel generators with fuel.
2.0.2 | The tank shall be manufactured from carbon steel with thickness as U.L. Standard 142.
2.0.3 | The tank shall be externally coated with 2 layers of coatings. The prime layer using Red Oxide paint and the top layer using water proof plastic layer. Additional protection layer on top of the fuel tank.
2.0.4 | Tank shall comply with the normal and emergency venting requirements NFPA 30.
2.0.5 | Fuel tank to have, lowest point drain facility for water and sludge, fuel level gauge direct mounted or remote electric, filler pipe and locking cap.
2.0.6 | The design criteria shall conform to the following minimum requirements: Steel Pipe: ASME B36.10, Schedule 40 Black Steel Fittings: ASTM B16.3, 300 lb. Threaded malleable iron, or ASTM A234, forged steel welding type. Finish: Prime and finish paint with industrial enamel.
2.0.7 | Welding shall be carried out in accordance with an approved standard or code of practice. The welding plants and processes used shall be suitable to the materials, configurations and purposes of the welded parts. Only qualified welders, certified for the type of welding required, shall be employed. The Contractor shall exercise strict control over the welding conditions and parameters and shall continuously monitor the standard of welding achieved in accordance with the requirements of the Clause on Quality Control and Quality Assurance.