## LOT 1 DOWD
ANNEX 1 TECHNICAL SPECIFICATION
PN:19.1801.0-004.00
A. Technical Specification
LOT 1: Water Disinfection Equipment and Spare Parts for Directorate of Water Duhok Outskirts
.No | Description | Unit | QTY
1 | chlorination dosing system including 1-Dosing pump 24L/h presuure 10 bar 380 V Protection 55 l.P. dosing head PVC with maintaing set (inlet. outlet ball valve diaphragm) 2-Poly atheline container 300 L including 3/4 inch cleaning valve made of pvc 3-section line pvc includes foot valve with strainer 4-injection unit with pressure spring hose of 10 m length 15 bars 5-Protect masks (2 units) including filter 6-Manual agetator 7- control panel including phasifiler | pcs | 10
2 | Diaphragm 64 mm compatible to fit for chlorine solution dosing pump Jesco-E-24 of 10 bars. | pcs | 50
3 | Injection Unit ball valve with pressure spring of 1.2bar compatible to fit to dosing pump of ALLDOS DMX 24 95730912 hose connection | pcs | 60
4 | Dosing head made of P.V.C suitable for chlorine solution compatible to fit to the dosing pump ALLDOS DMH24 98961635 (6 Screws connection) | pcs | 10
5 | Gas Dosing regulator Full vacuum dosing regulator for exact chlorine gas dosing up to a max. of 1000 g/hr volume flow rate of the chlorine gas is set with the dosing regulator includes integrated rotary flow meter vacuum connections for input and output for PE tube 8/11 mm with gas flow meter VGA-113-1000 or equivalent | pcs | 10
6 | Vacuum regulator for gas chlorinator 4 kg/h to be connected directly to the chlorine gas cylinder connection with binding key and pressure gauge C111 or equivalent | pcs | 10
7 | Chlorine Injector dosing quantity for Cl₂ 1 kg/h backpressure: 0-7 bar (545-1000-1) or similar | pcs | 5
8 | Chlorine solution hose for dosing pump diameter 6/12 mm 3 m length Pressure of10 bars | pcs | 60
9 | Inlet and outlet ball valve with connection accessories for chlorine solution compatible to fit to Dosing pump Jesco-E-24 | pcs | 50
10 | Inlet outlet ball valve with connection accessories for chlorine solution compatible to fit to dosing pump ALLDOS -DMX 221 and DMH 251-24 | SET | 50
11 | Pool tester for chlorine and ph analysis chlorine range of 1 - 10 ppm Plastic case containing the tube with colorimetric scale | pcs | 20
12 | LED Turbidimeter TL2360 ISO, 0-10000 NTU Accuracy: FNU: ±2% of reading plus 0.01 FNU from 0 - 1000 FNU FAU: ±10% of reading from 20 - 10000 NTU NTU: ±2% of reading plus 0.01 NTU from 0 - 1000 NTU, ±5% of reading from 1000 - 4000 NTU, ±10% of reading from 4000 - 10000 NTU H X W X B (mm) 153 mm x 395 mm x 305 mm Range:0 – 10000 NTU Accuracy: Absorbance: ±0.005 Abs from 0 - 1 Abs at 860 nm Operating Temperature Range:0 - 40 °C Certification: CE, KC, RCM Warranty: 12 months Weight:3.0 kg | pcs | 1

## LOT 2 DoW
ANNEX 1 TECHNICAL SPECIFICATION
PN:19.1801.0-004.00
A. Technical Specification
LOT 2: Laboratory and Sterilization Equipment for the Directorate of Water for Duhok Governorate
item | Description | unit | Qty
1 | Copper Line chlorine line copper nikal coated 2.00 m length both end union connection 1" | pcs | 12
2 | Aluminium Sulphate Dosing Pump Grundfos DMH 1500-4, S/N; 11/128145 OR equivalent Nominal flow rate at 50 Hz 1500 l/h Number of dosing heads: 1 CE Certificate Non return valve type 1 inlet pump and not spring-loaded Max viscosity: 5 mPas Pump housing made of Aluminium Maximum operating pressure at 4 bar Type of inlet and outlet connection is welding Pumped liquid is Water Selected liquid temperature about 20 °C Density 998.2 kg/m³ Power input P1:1,100 kW Mains frequency:50 Hz Rated voltage:3 x 230/400 V, 50 Hz, 460 V, 60Hz V Enclosure class (IEC 34-5): IP 65/F Power plug: NO CABLE Mains cable: NO CABLE m Protection level IP 55 factory preset and tested according to factory standard | pcs | 2
Intrastat commodity code 8435040 motor type:three-Phase current motor capacity:1.100kw Dosing head material:V4A Dosing head size :7 valve suction side gasket:FKM, material:V4A ball:316L seat:satinless steel 316Ticonnection:flange DN32 pressure release:0.00Bar valve discharge side gasket:FKM, material:V4A ball:316L seat:satinless steel 316Ti connection:flange DN32 pressure release:0.00Bar pump gearbox gear ratio 9,75:1, pump enclosure standard material:aluminum, stroke adjustment manual pressure relief valve: 10 bar nominal width: DN32, pressure 10.000 bar, connection: flange DN32 material: V4A, pipe: 11/4 gear oil: DHG68, 5lt documentation: instruction manual, multilingual
3 | Injector to draw from chlor Type 545-0715-10000 Grundfos or equivalent Capacity 40 kg/h with application: standard pressure range: 0-10 bar backphragm:0-10.0 bar output connection DN50 | pcs | 2
4 | Metlic pipe for chlorine gas size: 1 inch Anti-chlor length:5m pressure: 16bar | pcs | 12
5 | Gear oil 5 lt 96607809 555-305 or equivalent suitable and compatible for dosing pump of alldos-Grandfos 1500L capacity | pcs | 3
6 | Gear Oil 750 mL suitable for Jesco Dosing pumps ISO-VG 460 (SAE140) or equivalent | pcs | 2
7 | Gas Dosing Regulator VGB 103 /1-S-1-O,BOX or equivalent 1000 g/h Gas Dosing system in cloding flow meter 1000g/h outside filter connected directly to Clorine gas Cylinder | pcs | 2
8 | Booster Pump CR 5-13 A-A-A-E-HQQE or equivalent Vertical, multistage centrifugal pump with suction and discharge ports on the same level. The pump head and base are in cast iron - all other wetted parts are in stainless steel (EN 1.4301) Rated flow 5.8 m³/h Rated head 66.1 m Maximum head 88.4 m Stages 13 Impellers 13 Pump orientation Vertical Shaft seal arrangement Single t max amb 60 °C Maximum operating pressure 16 bar Max pressure at stated temp 16 bar / 120 °C 16 bar / -20 °C Pumped liquid Water Liquid temperature range -20 .. 120 °C Selected liquid temperature 20 °C Motor standard IEC Motor type 90LE | pcs | 2
IE Efficiency class IE3 Rated power - P2 2.2 kW Power (P2) required by pump 2.2 kW Mains frequency 50 Hz Rated voltage 3 x 380-415D V Rated current 4.65 A
9 | flat gasket blue/green inner diameter 7.50 mm outside diameter 20.00 mm material thickness 2.50 mm 91835768 or equivalent | pcs | 750
10 | Chlorine gas protection mask With Filter | pcs | 12
11 | suction line 96728483 or equivalent nominal width: DN8 Material: PVC 0,500 kg suitable for 300 lt with foot valve compatible for dosing pumps from ALLDOS | pcs | 10
12 | Pump Connection set Alldos/grundfos 529-043 or equivalent nominal width: DN8 pressure: 10 bar pump connection: G5/8 material: PVC pipe: 10/12 for PE hose 4/6, PVC hose 4/6, PVC 6/12 | pcs | 15
13 | Valve gasket grundfos/alldos FKM ball:glas connection: 5/8' pressure relief spring: 1.5 bar | pcs | 12
14 | Hose 91835686 grundfos/alldos or equivalent Material: PVC Tube size: 6/12 mm Length: 50 m Maximum operating presssure: 23 bar | pcs | 15
15 | Photometer for water analyzes Lovibond multidirect or similar Operation: Acid and solvent resistant, touch-sensitive keypad with audible feedback Display; Graphic-display Interfaces : RS 232 Auto-Check; By pressing ON/OFF-key Updates: Software and methods update by means of the internet Internal Storage: approx. 1000 data sets with date, time and registration number Power Supply: 7 NiMH-battery pack (AA/Mignon) Auto – OFF: Yes Portability: Benchtop Environmental Conditions: up to max. 90 % humidity (non condensing) approx. 5 - 40 °C Compliance: CE Dimensions: 265 x 70 x 195 mm Weight: 1000 g (with rechargeable batteries) | pcs | 1
16 | Flame Photometer BWB Flame Photometer or equivalent sample rate: 3.5-5 ml/min ions measured: alkali earth metals Sodium(Na) Potassium (K) lithium (Li) Calcium (Ca) and Barium (Ba) instrument size: 51 x 38 x 41 cm optimal range: Na, single point calibration 0.1 - 60 ppm, multipoint calibration 0.1 - 1000 ppm K single point calibration 0.05 - 100 ppm, multipoint calibration 0.05 - 1000 ppm Li single point calibration 0.05 - 50 pp, multipoint calibration 0.05 - 1000 ppm Ca single point calibration 1.0 - 100 ppm, multipoint calibration 1.0 - 1000 ppm time to stability: less than 15 sec after sample is introduced to the flame Interfaces: USB, 0-2.5 Volt output (based on sample concentration linked to element of user's choice optional integrated printer power requirements: 100 V - 250 V AC at 50 or 60 Hz automatically selecting Fuel used can be Propane, Butane or Natural Gas regulated to 19 bar, flow rate of 0.4 l/min | pcs | 1
accessories inlcuded: PC Leads USB, power lead, gas hose, aspiration kit, Manuals covering all aspects of the XP Plus FP, Quick Start guides, Warranty Registration Form, Certificates of analysis for all provided Fluids, Material Safety Data Sheets for all provided Fluids, The FP-PC Software installation USB, 150ml of BWB recommended cleaning solution, 150ml calibration fluids for 4 elements at 10,000ppm. 150ml calibration fluid for internal reference standard (Cs) at 10,000ppm 100ml conical flask with screw lid 100 disposable sample cups 1L of De-Ionised water 2m of waste tube Set of spare fuses 10 x 10ml pipettes 10 x 1ml pipettes
17 | Nitrate Tube Test Reagent Set every packet contain 50 cells with tests Lovibond 535580 or equivalent | pcs | 3
18 | Sulphates Reagents fitting to for Lovibond 535580 device / every packet contain 100 bags | pcs | 2
19 | Turbidity measurement device (10000) NTU WTW Lab Turbidity Meter 555 or equivalent High-end laboratory turbidity meter, with tungsten lamp in accordance with US-EPA single unit with calibration standard set (0,02 - 10,0 - 1000 NTU) 3 empty cuvettes optional continuous flow measurement with the flow vessel D-Turb or flow-Thru to 1 bar Calibration: Automatic 1...5 point calibration | pcs | 1
20 | Turbidity measurement device (0.1 - 800) NTU TB 300 IR or similar Turbidity is measured according to EN ISO 7027 by nephelometric means (90° scattered light) ± 2 % of reading, or ± 0.01 NTU, whichever is bigger, in the range of 0.01 - 500 NTU ; ± 5 % of reading in the range of 500 - 1000 NTU acid and solvent resistant; membrane keypad Display: Graphic-Display Suitable Vials: Round Cuvettes 24 mm Calibration: automatic overall range adjustment with Standard-Set T-Cal Internal Storage 1000 data sets Measuring Range 0.01 - 1100 NTU (Autorange) Compliance CE Dimensions 265 x 195 x 70 mm Instrument is carried in a case, including 1 Set of turbidity standards T-CAL 7 Rechargeable batteries (AA) 1 Lithium battery Mains charger 100-240 V | pcs | 1
PC Connection cable 4 Vials (ø 24 mm) with lids Warranty information Certificate of Compliance Instruction Manual
21 | Mobile Turbidity meter WTW Turb 430 or similar (1000 )NTN Portable turbidity meter (90 °) with infrared light source according to DIN EN 27027 including standard set in box case with tray and accessories. Accessories: Calibration set (0,02 - 10,0 - 1000 NTU), 4 sample vials 28 mm, cleaning cloth, screwdriver, PC software LSdata, PC connection cable AK 540 B, instructions. Optional: Labstation LS Flex/430 with PC software LSdata for GLP-compliant data evaluation or Battery Pack RB Flex/430. | pcs | 1
22 | Lab PH Meter inoLab pH 7110 Easy-to-operate basic pH/mV benchtop meter with DIN socket for routine measurement. For AC and battery operation. Meter with universal power supply, stand and operation manual. Range / Resolution pH -2.0...20.0 ±0,1 pH -2.00...20.00 ±0.01 pH -2.000...19.999 ±0.005 pH mV ±(1200.0 ±0.3) mV Temp. ±(2000 ±1) mV Active AutoRead function Easy calibration with adjustable calibration timer Intuitive operation with clearly arranged keypad including bafer solution ph (4.7.10) | pcs | 1
23 | Mobile Water Analysis SensoDirect 150 or similar for determination of dissolved oxygen (O2), O2 concentration, conductivity, TDS, pH and ORP ph/Redox, Conductivity, Dissolved Oxgen, TDS, Temperature (°C/°F) All in one Large digital display Protective casing Display Large LCD display with contrast adjustment Power Supply DC 1,5 V battery (UM3,AA) DC 9 V adapter Auto – OFF Yes Portability Portable Compliance CE Protection Class IP 51 Dimensions 120 x 40 x 220 mm Weight 625 g (unit incl. batteries) Weight with Packaging (unit incl. batteries) Conductivity 0 - 200 µS/cm Conductivity 0.2 - 2.000 mS/cm Conductivity 2 - 20 mS/cm Conductivity 20 - 200 mS/cm Oxygen 0 - 20 mg/L O2 pH 0 - 14 | pcs | 1
TDS 0 - 132 ppm TDS 132 - 1320 ppm TDS 1320 - 13200 ppm TDS 13200 - 132000 ppm Temperature 0 - 60 ° C Delivery Content: instrument batteries pH eletrode temperature probe conductivity probe Oxygen sensor pH buffer set 4,01/7,00 electrolyte membrane heads instruction manual, warranty Information
24 | Pipette 10 ml Calibrated To Deliver (TD) to the tip Sterile, non-pyrogenic, and DNase/RNase-free Pipets have a uniform pulled tip and are clean, plugged, sterile and ready for use Color coding for visual confirmation of correct pipet capacity Provided with "negative" graduations to increase the versatility of the pipet Beveled or molded top ends Irradiation sterilized for use with tissue culture work | pcs | 7
25 | Purple Broth Medium MacConkey Lab005 or equivalent used in the detection and enumeration of faecal coliforms (37°C) and E. coli (44°C) The replacement of neutral red used in the original formulation by bromocresol purple makes the colour change caused by acid producing organisms easier to read | lt | 1
26 | DPD Tablets for Water Testing Lovibond or equivalent 500 tablets for measuring Chlorine levels to use for drinking water and industrial process water. | pcs | 10