## Technical Specifications
ANNEX 1 TECHNICAL SPECIFICATION
PN:19.1801.0-004.00
A. Technical Specification
Item No. | Description | Unit | Quantity
Supply of Submersible pumps and Motors
1 | Intake submersible pump: Supplying a Surface water intake submersible pump the pumps should be for river raw water ( A steel structure intake will be installed on Khbur river, the submersible pumps shoud jet the water from the river to the compact unit), The pump should be with all needed fitting and accsesories to install the pumps over the intake bridge. The head of the each should be 140m, with capacity of 60m3\h. The pump should be according to spisification of CR 64 Pump orientation: Vertical. Shaft seal arrangement: Single Curve tolerance: ISO9906:2012 3B Materials Base: Cast iron, EN 1563 EN-GJS-500-7, ASTM A536 80-55-06 Impeller: Stainless steel, EN 1.4301, AISI 304 Bearing: SIC Support bearing: Graflon Installation Maximum ambient temperature: 55 °C Maximum operating pressure: 30 bar Max pressure at stated temp: 30 bar / 120 °C 30 bar / -30 °C Type of connection: DIN Size of inlet connection: DN 100 Size of outlet connection: DN 100 Pressure rating for connection: PN 40 Flange size for motor: FF350 Liquid temperature range: -30 .. 120 °C Density: 998.2 kg/m³ Electrical data Motor standard: IEC 34-5) IP 55 IE Efficiency class: IE3 Rated power : (P2 ) 37 kW Power (P2) required by pump: 37 kW Mains frequency : 50 Hz Rated voltage: 3 x 380-420D/660-725Y V Rated current: 68,0-63,0/39,0-36,0 A Requested voltage: 400 V Rated current at this voltage: 65.5 A Starting current: 670-670 % Cos phi - power factor: 0.88 Rated speed: 2955 rpm Efficiency: IE3 93,7% Motor efficiency at full load: 93.7-93.7 % Motor efficiency at 3/4 load: 93.9-93.9 % Motor efficiency at 1/2 load: 93.5-93.5 % Motor voltage : 380volt, 50 Hz Electrical: 3phase Number of poles: 2 Enclosure class: (IEC 34-5) IP55 Insulation class: (IEC 85) F Motor protec: PTC Controls Minimum efficiency index: MEI ≥0.70 Net weight: 354 kg Gross weight: 398 kg Shipping volume: 0.808 m³ | pieces | 4
B. Delivery
All Items should Be delivered to GIZ Construction unit warehouse /Iraq/ Duhok
C. Remarks And Condition
1 | Certification of origin for all offered items should be provided before delivery.
2 | Submit Manufacturer certification and test reports for all offered items should be provided before delivery.
3 | Catalogues (should be European Brand or equivalent Brand) and tech. specifications should be provided with offers .