## Technical Bid
Annex A 1-Technical Bid Form
Extension of Storm water Sewer UPVC Pipeline and surface drainage for the main street of Al Shaheed Wadah and Hay Al Chanaien in Qatoon-Baqubah District مد انابيب مجاري مياه الامطار و مجاري سطحية للشارع الرئيسي لمنطقة الشهيد وضاح و حي الجناين في الكاطون - قضاء بعقوبة
Project Location
Governorate |  | Diyala | Sub-district | Baqubah |  | GPS Coordinates
District |  | Baqubah | Town/Village | Qatoon |  | 33.7331 |  |  | 44.6077
All material must be heavy-duty type. All supplied accessories and materials require sampling provision prior acceptance by the supervising engineer. All structural concrete work must be according to ACI 318M-2014 code, and all work must be according to the Iraqi Technical standards, and DRC’s engineer instructions.
Item | Description |  |  | المواصفات | Unit | Qty | Offered Units | Offered Quantities | Description | Origin Made
1 | UPVC Pipes with Excavation and backfill Works: Supply, excavate, extend, burying, test, connect and operate UPVC pipeline pressure of (6 bar) with rubber attachments successful in laboratory tests (DIN 8061 & 8062) and the materials needed to implement sewer lines. The price includes the transportation of pipes, drilling the line with extend and pressing the pipes with supply sand-gravel mixture class (B) supported by its success in a laboratory to covered the pipe from all directions thickness (30) cm with good compaction by using a small mechanical compacting machines under the pipe and to a level of 60 cm above the pipe with pull of groundwater according to requirement of the site. The line should be free of water with cleaning the pipe from mud sediments in addition to backfill (bury) the path of the line with a layers of clean soil (25 cm thickness for each layer) with good compaction by using mechanical compacting machines to the level of ground with ratio 95% that match laboratory test, settlement the site and return street to what it was, according to the road specifications and general standard specifications of sewer (DoS), the price includes all necessary laboratory tests and wages of street cracking by using (Cutter machine). The path of the excavation line must be surveyed and reflected to (GIS) and according to instruction of supervisor engineer. |  |  | أنابيب UPVC مع اعمال الحفر والدفن: تجهيز وحفر ومد ودفن وفحص وربط وتشغيل انابيب بلاستك UPVC ضغط (6 جو)، مع الملحقات المطاطية على ان يكون ناجح في الفحوصات المختبرية (DIN 8061 & 8062) والمواد اللازمة لتنفيذ خطوط المجاري, ويشمل السعر أجور نقل الانابيب مع حفر الخط مع مد وكبس الانابيب مع تجهيز حصى خابط صنف (B) مؤيدة بنجاحه مختبريا لتغليف الانبوب من جميع الجهات وبسمك 30سم مع حدلها جيدا بواسطة الحادلات الميكانيكية الصغيرة تحت الانبوب والى مستوى 60 سم فوق الانبوب مع سحب المياه الجوفية حسب متطلبات موقع العمل على ان يكون مسار الحفر خالي من المياه مع تنظيف الانبوب من الترسبات الطينية بالاضافة الى اعادة دفن مسار الخط بالتراب النظيف وبطبقات وبسمك 25 سم للطبقة الواحدة مع الحدل الجيد باستخدام الحادلات الميكانيكية الى مستوى الارض وبنسبة 95 % مؤيدة للفحوصات المختبرية مع تسوية الموقع واعادة الشارع على ما كان عليه بموجب مواصفات الطرق ويكون العمل بموجب المواصفات القياسية العامة للمجاري, ويشمل السعر اجور كافة الفحوصات المختبرية اللازمة واجور تكسير الشارع باستخدام الكتر ,مع تثبيت الخطوط بنظام (GIS) وحسب توجيهات المهندس المشرف. | [5 empty] | N/A
| 1- Supply UPVC sewer pipe line (6 bar) ,315mm diameter, 6-m length and average depth (1.5 - 2.5)m. To be purchased and entered into warehouse of DoS. |  |  | ا- تجهيز خطوط مجاري UPVC (6 بار) ، قطر 315 ملم ، طول 6 م و بعمق يتراوح (1.5-2.5) م. على أن يتم شرائها وأدخالها مخزنيا. | M.L | 225
| 1- Supply UPVC sewer pipe line (6 bar) ,250mm diameter, 6-m length and average depth (1.5 - 2.5)m. To be purchased and entered into warehouse of DoS. |  |  | ب-تجهيز خطوط مجاري UPVC (6 بار) ، قطر 250 ملم ، طول 6 م و بعمق يتراوح (1.5-2.5) م. على أن يتم شرائها وأدخالها مخزنيا. | M.L | 90
| 2- Supply UPVC sewer pipe line (6 bar) ,200mm diameter, 6-m length and average depth (0.9 - 1.2)m. To be purchased and entered into warehouse of DoS. |  |  | ج-تجهيز خطوط مجاري UPVC (6 بار) ، قطر 200 ملم ، طول 6 م وبعمق يتراوح (0.9-1.2) م. على أن يتم شرائها وأدخالها مخزنيا. | M.L | 530
2 | Main Manholes: Supply materials to be laboratory successful and working to pour the main circular manholes of sewage lines from reinforced concrete resistant to salts with a mixing ratio of 3: 1.5: 1 (30 MPa), and a thickness of the walls and ceiling 25 cm, thickness of the floor 50 cm, the price includes the costs of laboratory tests, pull groundwater and casting a layer of (blinding) from the usual concrete resistant to salts with a thickness of 10 cm. The work should be using a moisture inhibitor (Flankot) on the outside, and an epoxy with sealant (water stope) on the inside, with fixing the pipe to the ordinary concrete resistant to salts according to the drawings and instructions of the supervisor engineer. |  |  | المنهولات الرئيسية: تجهيز مواد على ان تكون ناجحة مختبريا وعمل لصب المنهولات الرئيسية الدائرية لخطوط المجاري من الخرسانة المسلحة المقاومة للاملاح وبنسبة خلط 3:1.5:1 (30 ميكا باسكال )وبسمك للجدرا ن والسقف 25 سم وبسمك للأرضية 50 سم, ويشمل السعر أجور الفحوصات المختبرية وسحب المياه الجوفية وصبة طبقة (blinding) من الخرسانة الاعتيادية المقاومة للاملاح بسمك 10 سم ويكون العمل باستخدام مانع الرطوبة (الفلانكوت) من الخارج والايبوكسي من الداخل ومانع التسرب (water stope) مع تثبيت الانبوب بالخرسانة العادية المقاوم للاملاح وفق المخططات وتوجيهات المهندس المشرف. | [5 empty] | N/A
| a- Manhole with internal diameter (1.1)m for sewer line 315mm with average depth 2 m, 9 manhole. |  |  | أ- منهول قطر داخلي (1.1) م لخط المجاري 315 ملم بمعدل عمق 2 م عدد9 منهول. | No. | 9
| b- Supply, install and fixing the round iron cover with the base (55) cm diameter from heavy duty. (Similar to Brisko brand or equivalent ) connected to the frame by a heavy duty hinges. |  |  | ب- تجهيز وتثبيت وتركيب الغطاء الحديدي المدور مع القاعدة قطر (55) سم من النوع الثقيل (مشابه لBrisko او ما يماثله) و مربوط بالاطار بواسطة نرمادات من النوع الثقيل | No. | 9
3 | Gully Side (Street Gutters): Supply materials to be successful with laboratory tests and work to pour the side gully of plain concrete resistant to salts with a mixing ratio of 3: 1.5: 1 and thickness of the walls and floors (15) cm, internal dimensions (90x35x25) cm. the work includs Supply, install and fixing steel of grid cover with the base and dimensions (38x28) cm of heavy duty type. |  |  | الكليات الجانبية: تجهيز مواد على ان تكون ناجحة بالفحوصات المختبرية وعمل لصب الكليات الجانبية من الخرسانة الغير مسلحة المقاومة للاملاح وبنسبة خلط 3:1.5:1 وسمك للجدران والارضية (15) سم وبأبعاد داخلية (90x35x25) سم. العمل يشمل تجهيز وتثبيت وتركيب المشبك الحديدي مع القاعدة وبابعاد (38x28) سم من النوع الثقيل. | No. | 41
Delivery time required (days after the site handover): |  |  | 45 working Days | Delivery time offered (days after the site handover):
Delivery Terms required (Add Incoterm if necessary): |  |  | DDP INCOTERMS 2020 | Delivery Terms offered (must include incoterm):
Delivery Destination required: |  |  | Hay Al Chanaien in Qatoon-Baqubah District | Delivery Destination offered:
Minimum bid validity period required: |  |  | 90 Days | Bid validity period offfered:
Currency of Tender: |  |  | USD only | Currency of Bid:
Materials type: All material must be heavy-duty type. All supplied accessories and materials require sampling provision prior acceptance by the supervising engineer. All structural concrete work must be according to ACI 318M-2014 code, and all work must be according to the Iraqi Technical standards, and DRC’s engineer instructions. |  |  | Yes / No | Materials type: All material must be heavy-duty type. All supplied accessories and materials require sampling provision prior acceptance by the supervising engineer. All structural concrete work must be according to ACI 318M-2014 code, and all work must be according to the Iraqi Technical standards, and DRC’s engineer instructions. | YES / NO
▸ The bidder is responsible for placing danger signals and creating a large panel for the project. • All works are in accordance with the general conditions of Iraqi contracting and engineering work. • The bidder must maintain the safety of the on-site staff and beneficiaries and provide safety supplies. • The bidder must ensure that his team is committed to respecting the customs and traditions of the community in which they work. • The bidder must provide samples of materials and equipment to be used for work and obtain the approval of the engineer supervising the type and origin. • The bidder complies with all the conditions stipulated in the contract with a timetable for the implementation of the project and as directed by the supervising engineer. • The maintenance warranty period will be 3 months. |  |  |  | Company Name:
Signed by a duly authorized company representative:
Title:
Date:
Print Name:
Stamp of company
Note on I5: Author: Latitude
Note on L5: Author: Longitude