## Annex A 1-Technical Bid Form
Annex A 1-Technical Bid Form
Project Title: |  | Rehabilitation of Bakhtiary Water Project-Khanaqin district أعادة تأهيل مشروع ماء بختياري - قضاء خانقين
Governorate |  | Diyala | Sub-district | Khanaqin |  | GPS Coordinates
District |  | Khanaqin | Town/Village | Backteiary |  | 34.3131 |  |  | 45.3585
1- All the provided materials must be of heavy duty and from reputable company/reliable brands. 2- Samples of pipes, fittings, wires and the electrical switches must be provided for approval. 3- All the imported material like pumps, dozers, mixers, switches and wires) must accompanied by a proper / clear certificate of origin indicated the brand, model, date of entry, specification of the material with clear/proper test certificate. For the pumps and the valves a catalogue and data sheet must be provided. 4-DRC's representatives, whenever request, shall visit the materials suppliers shops/manufacturers to confirm the provided quality of the materials and match it with certificates of origin and the test certificates. 5- All the work must be done according to the Iraqi/international technical standard under the direct instructions and supervision of DRC. 6- Coordination with DoW required (through DRC), permission for inspections and acceptance of items/equipment by DoW officials is to be included within the work schedule. 7- All the provided materials and the old ones must be entering/out and transported to the warehouse of DoW according to the instruction of the supervisor engineer. 8- The contractor must clean all the site (walkways, gardens, Old equipment etc....) after completing all the works on-site to ensure proper environment. 9- The contractor must install a project ID after project completion shows the rehabilitated Items done by DRC. 10- the supplier should be guaranteed the all tank at least 6 months after installation.
Item | Description |  |  | الوصف | Unit | Qty | Offered Units | Offered Quantities | Description | Origin Made
1 | Rehabilitation of the Wells which provide water |  |  | اعادة تأهيل الابار المجهزة للماء
2 | Submersibles Pump replacement for wells: Provision of materials, equipment, tools, and manpower to perform the work of replacing the submersible pump which have the specification of 11 kilowatts (50 Hz, 3phase 380-420 V, 2800-2900rpm, IP68), similar to "lowara" or "Grundfos" submersible pump specifications or equivalent of 3 inch size, 12 stages, and stainless steel impeller. The pump must be equipped with electrical cable (4 x 6) mm2 size and a length of more than 65 m and compatible starter. The work includes lifting the old submersible pump from the wells and installation th new one, make a proper electrical connection, and everything necessary to complete the work to ensure perfect operation according to the technical specifications of the manufacturer of th submersible pump and directives of the supervising engineer. |  |  | استبدال غواطس الابار تجهيز المواد و المعدات والادوات للقيام باعمال استبدال غواطس الابار بمواصفات 11 كيلو واط (50 هرتز, 3 فيز 380-420 فولت ,2800-2900 دورة بالدقيقة, IP68),مشابه مواصفات المضخات الغاطسة نوع "لوارا" أو "كروندفوس" أو ما يعادلها مع المضخة حجم (3 انج) ذات 12 مرحلة (بشارة نوع ستيل), يجب أن تكون المضخة مزودة بكابل كهربائي مقاس (4 × 6) ملم2 وبطول يزيد عن 65 م وبادئ تشغيل متوافق. يشمل العمل رفع المضخة الغاطسة القديمة من الآبار وتركيب المضخة الجديدة وعمل توصيل كهربائي مناسب وكل ما يلزم لإتمام العمل لضمان التشغيل المثالي حسب المواصفات الفنية للشركة المصنعة للمضخة الغاطسة وتوجيهات المهندس مشرف. | No | 3
3 | Voltages regulator for the wells: Provide the materials, equipments, tools, and manpower to install, and operating a new Voltages Regulator into the water wells station with capacity 45 KVA (similar to Al-Hadarah type) 3-phases, with necessary modification and maintenance needed for the electrical boards and the electrical connections to completing the works and operating the submersible pumps perfectly and according to the technical specifications of the manufacturer and the instructions of supervision engineer |  |  | منظم الفولتية للآبار: توفير المواد والمعدات والأدوات والقوى العاملة لتركيب وتشغيل منظم الفولتية جديد في محطة آبار المياه بطاقة 45 كي في أي (مماثل لنوع الحضارة) 3 فيز مع التعديلات اللازمة والصيانة اللازمة للوحات الكهربائية والتوصيلات الكهربائية لانجاز الاعمال وتشغيل المضخات الغاطسة بشكل كامل وحسب المواصفات الفنية الخاصة بالصانع وتعليمات مهندس الاشراف | No | 6
4 | Sterilization System |  |  | منظومة التعقيم
| Chlorine device: Provide the materials, equipments, tools, and manpower to install and operate a new chlorine device of 2 Kgm/ hr. capacity with injector type Aldose or equivilant. The work includes all connections accessories of copper pipes, bronze locks and a complete network of PVC pipes 16 bar, 25mm diameter with the heater, metal pipe from the bottel to the device with the lock, bends, divisions, and gas filter. All mechanical connections is required to ensure proper installation, and all electrical connections should be done with the main electrical board to ensure full control of the system. Install a warning device in case of chlorine leakage happening with all the necessary required pipes for that and all the works required to complete the Job perfectly and ensure full functionality of the system. |  |  | جهاز الكلور: توفير المواد والمعدات والأدوات والقوى العاملة لتركيب وتشغيل جهاز الكلور الجديد 2 كجم / الساعة. السعة مع حاقن من نوع Aldos أو ما يكافئة. يشمل العمل جميع ملحقات توصيلات الأنابيب النحاسية والأقفال البرونزية وشبكة كاملة من الأنابيب (PVC) 16 بار قطر 25 مم مع السخان وانابيب معدنيه من القنينة للجهاز مع القفل والانحناءات والانقسامات وفلتر الغاز. جميع التوصيلات الميكانيكية مطلوبة لضمان التركيب الصحيح ، ويجب إجراء جميع التوصيلات الكهربائية مع اللوحة الكهربائية الرئيسية لضمان التحكم الكامل في النظام. تركيب جهاز تحذير في حالة حدوث تسرب الكلور مع جميع الأنابيب اللازمة لذلك بالأضافة الى جميع الأعمال المطلوبة الاخرى لإكمال المهمة على أكمل وجه وضمان الأداء الوظيفي الكامل للنظام. | No | 1
5 | Booster pump: Supply, install and connect a new poster pump of 2.2 KW, 50Hz, 2 m3/h capacity and pressure(8-bar) H = (80-120)m with the starter , the works includes all cables connections from the electrical source to the starter, new steel fram (box ) and board to install all of the chlorine equipment's like (injector, booster, pipes,etc...) on the new unit for the steel from with all accessories of electrical and mechanical connections and connecting it with the main electrical board of the project, and all the works required to complete the Job. |  |  | مضخة البوستر: تجهيز وتركيب وربط مضخة بوستر جديدة 2.2 كيلوواط ، 50 هرتز ، 2900 دورة في الدقيقة ، Q = (2) م 3 / ساعة ، H = (80-120) م ، سعة وضغط من (8) بار ، مع الستارتر يشمل العمل كافة توصيلات الكابلات الكهربائية من مصدر الطاقة إلى الستارتر، إطار فولاذي جديد (كابينة) مع لوح لتركيب جميع معدات نظام الكلور مثل (الحاقن ، بوستر ، الانابيب ، إلخ .. على الوحدة الجديدة للإطار واللوح مع جميع ملحقات التوصيلات الكهربائية والميكانيكية وجميع الأعمال المطلوبة لإكمال المهمة. | No | 1
6 | Chlorine powder system: Supply, install and operat a chlorine powder sterilization system that includes an injector with specifications (350-400) liters per hour and a 0.75 kilowatt mixer, a tank with a capacity of 1000 liters with all the necessary pipe connections from the system to the pipe for pumping water to the beneficiaries, the work includes all the necessary accessories of the starter inside a box with dimensions (40 x 60) cm and a triple circuit breaker of 100 A with digital measurements for voltage, current, etc.... And all that is necessary to complete the work according to the technical specifications and the directives of the supervising engineer. |  |  | منظومة مسحوق الكلور : تجهيز و نصب و تشغيل منظومة تعقيم بمسحوق الكلور تشمل حاقن بمواصفات (350-400)لتر/ساعة و خلاط 0,75 كيلو واط مع خزان بسعة 1000 لتر مع كل توصيلات الانابيب اللازمة من المنظومة الى الانبوب الخاص بضخ الماء الى المستفيدينن, يشمل العمل كافة الملحقات اللازمة من ستارتر داخل بوكس بابعاد (40×60) سم و قاطع ثلاثي 100 امبير مع المقاييس الدجيتال الخاصة بالفولتية والتيار الخ.... و كل ما هو ضروري لانجاز العمل حسب المواصفات الفنية و توجيهات المهندس المشرف | No | 1
7 | Sprinkler with Pipes: Supply and connect 1.5 inch diameter galvanized iron pipes from the service line in the project to the submersible basin to make a sprinkler from the same pipe surrounding all the ribs with a shower measuring (0.5) inch with a height of 20 cm diagonally upwards every 1 m of the length of the ribs of the basin with each the necessary locks and accessories, according to the technical specifications and the directions of the supervising engineer |  |  | المرش مع الانابيب: تجهيز و ربط انابيب قطر 1.5 انج من الحديد المغلون من خط الخدمة في المشروع الى حوض التغطيس لعمل مرش من نفس الانبوب يحيط كافة الاضلاع مع عمل دوش قياس (0.5) انج بارتفاع 20 سم بصورة مائلة الى الاعلى كل 1 م من طول اضلاع الحوض مع كل ما يلزم من الاقفال و الملحقات و حسب المواصفات الفنية و توجيهات المهندس المشرف | ML | 40
8 | Supporting the Steel Structure with Lifting Pulley: Prepare materials and add I-Beam (5) angular section perpendicular to the existing structure to install a 1 ton mechanical lifting pulley with its chains. The price includes painting with radilite paint (two layers) and three layers of oil paint for the old and new structure, according to the technical specifications and the directions of the supervising engineer. |  |  | تدعيم هيكل فولاذي مع بكرة الرفع: تجهيز المواد و القيام اضافة مقطع حديدي نوع I-Beam (5) انج بشكل عمودي على جانبي الهيكل الموجود الحالي لتثبيت بكرة رفع ميكانيكية 1 طن مع السلاسل الخاصة بها. السعر يشمل الطلاء بطلاء الرادليت (طبقتين) و ثلاث طبقات من الطلاء الدهني للهيكل القديم و الجديد و حسب المواصفات الفنية و توجيهات المهندس المشرف | L.S | 1
9 | Rehabilitation of the WTU |  |  | إعادة تاهيل مشروع الماء
10 | Electrical cable: Provide, install, connect and operate a twist cable 3 x 50mm + 35mm size to deliver electric power to the project. The price includes the connection works of cable with the electrical power transformer and then installing it on the poles with all work requirements and according to the technical specifications and the instructions of supervision engineer. |  |  | كيبل كهرباء : تجهيز و نصب و ربط و تشغيل تويست كيبل (ظفيرة) حجم 3×50 ملم + 35 ملم لايصال التيار الكهربائي الى المشروع شاملا السعر اعمال الربط مع محول القدرة الكهربائي و من ثم مد الكيبل على اعمدة الكهرباء مع كل متطلبات العمل و حسب المواصفات الفنية و توجيهات المهندس المشرف | M.L | 420
11 | Electrical poles: Supplying and install a 9 m Galvanized circular iron electrical pole to providing the electric current to the project, the price includes digging the pole foundation and concrete casting for the column foundation with earthing using copper wire and coating work includes supplying and installing all necessary fastening accessories to install wires, according to the technical specifications and the directions of the supervising engineer. |  |  | اعمدة الكهرباء: تجهيز و نصب عمود حديد مغلون مدور 9 م لايصال التيار الكهربائي الى المشروع شاملا السعرحفر قاعدة العمود وصب قاعدة كونكريتية لاساس العمود مع التاريض باستخدام سلك نحاس و جميع ملحقات الربط الضرورية لثبيت الاسلاك و حسب المواصفات الفنية و توجيهات المهندس المشرف. | No | 10
12 | Voltage regulator for the project: Provide, install and operate a Voltage with capacity 20 KVA (similar to al Hadarah type) to be installed inside the water project building with the electrical connections and all necessary requirement to complete the work and according to the technical specifications and the instructions of supervision engineer. |  |  | منظم فولتية للمشروع : تجهيز و نصب و تشغيل فولتاج حجم (20) KVA (مشابه لنوع الحضارة) 3 فيز ليتم تنصيبه داخل بناية مشروع الماء مع التوصيلات الكهربائية وكافة المتطلبات اللازمة لاتمام العمل وحسب المواصفات الفنية و توجيهات المهندس المشرف | No | 1
13 | Lighting: Supply materials, equipment and work on re-operating the lighting poles, the work includes supplying and installing a LED light 250 watt and rewiring the lighting poles by using a cable (2×6) mm for external wiring and (2×2,5) mm for internal wiring, installing the lighting switches inside the main control board and according to the technical specifications and the instructions of supervision engineer. |  |  | الأنارة: تجهيز المواد و المعدات و العمل على اعادة تشغيل اعمدة الانارة شاملا السعر تجهيز و نصب مصباح لد 250 واط و اعادة تسليك اعمدة الانارة باستخدام كيبل 2×6 ملم للتسليك الخارجي و (2×2.5) ملم للتسليك الداخلي , و ربط مفاتيح خاصة بالانارة في لوحة السيطرة الرئيسية و حسب المواصفات الفنية و توجيهات المهندس المشرف | No. | 4
Delivery time required (days after the site handover): |  |  |  | 30 calendar days | Delivery time offered (days after the site handover):
Delivery Terms required (Add Incoterm if necessary): |  |  |  | DDP INCOTERMS 2020 | Delivery time offered (days after the site handover):
Delivery Destination required: |  |  |  | Khanaqin district | Delivery Destination offered:
Minimum bid validity period required: |  |  |  | 90 Days | Bid validity period offfered:
Currency of Tender: |  |  |  | USD Only | Currency of Bid:
Addaintional comments |  |  |  |  | Bidder to agree on additional comments: |  |  |  | Yes / No
1- All the provided materials must be of heavy duty and from reputable company/reliable brands. 2- Samples of pipes, fittings, wires and the electrical switches must be provided for approval before the installation. 3- All the imported material like pumps, dozers, mixers, switches and wires) must accompanied by a proper / clear certificate of origin indicated the brand, model, date of entry, specification of the material with clear/proper test certificate. For the pumps and the valves a catalogue and data sheet must be provided. 4-DRC's representatives, whenever request, shall visit the materials suppliers shops/manufacturers to confirm the provided quality of the materials and match it with certificates of origin and the test certificates. All materials that used on site must be subject to laboratory testing. 5- All the work must be done according to the Iraqi/international technical standard under the direct instructions and supervision of DRC. 6- Coordination with DoW required (through DRC), permission for inspections and acceptance of items/equipment by DoW officials is to be included within the work schedule. 7- All the provided materials and the old ones must be entering/out and transported to the warehouse of DoW according to the instruction of the supervisor engineer. 8- The contractor must clean all the site (walkways, gardens, Old equipment etc....) after completing all the works on-site to ensure proper environment. 9- The contractor must install a project ID after project completion shows the rehabilitated Items done by DRC. 10- the supplier should be guaranteed the all work 3 months except the tank, it will be 6 months after installation. |  |  |  |  | Company Name:
Signed by a duly authorized company representative:
Title:
Date:
Print Name:
Stamp of company
Note on I5: Author: Latitiude
Note on L5: Author: Longitude