## Annex A 2-Financial Bid Form
Annex A 2-Financial Bid Form
Project Title: |  | ITB-007DIY22 - Rehabilitation of AL-Moilha Water Treatment Plant Rehabilitation of AL-Moilha Water Treatment Plant 200 m3/hr اعادة تأهيل مشروع محطة ماء المولحة 200m3/hr
Project Location |  | BHA 606
Governorate |  | Anbar |  | Sub-district |  |  | Ameriat Al Fallujah |  | GPS Coordinates
District |  | Bazbaz |  | Town/Village |  |  | AL-Moilha |  | 33.1526 | 43.9563
Item | Description |  |  |  |  | الوصف | Unit | Qty | Offered Unit price (USD) | Offered Total Unit Price (USD)
A-1 | Intake System |  |  |  |  | منظومة السحب
A-1-1 | Low lift pump\ (intake): Supply, install, connect, test and operate new heavy-duty submersible pump, guaranteed for at least one year of operation (similar to Cabrari or equivalent) having the specifications as per the the following below: |  |  |  |  | مضخة السحب \ (المأخذ): تجهيز وتنصيب وتوصيل واختبار وتشغيل مضخة غاطس جديدة (للخدمة الثقيلة) مضمونة لمدة عام (مشابه لنوع كبراري او ما يكافئه) على الأقل من التشغيل مع المواصفات على النحو التالي: | No | 1
| a) Pump discharge Q= 220 m3/h, head=(20-30)m. | a) Pump discharge Q= 200 m3/h, head=20m. | a) Pump discharge Q= 200 m3/h, head=20m. | a) Pump discharge Q= 200 m3/h, head=20m. | a) Pump discharge Q= 200 m3/h, head=20m. | Q=(220) m3/h , H=(20 - 30)m
| b) Shaft and impeller made of stainless steel | b)Bronze impeller | b)Bronze impeller | b)Bronze impeller | b)Bronze impeller | شفت والبشارة مصنوع من الفولاذ المقاوم للصدأ.
| c) P= 22 KW, 380 V and 50 Hz r.p.m=1450-1500 | c) Motor power HP=30, RPM= 1450, Hz=50, V=400 and 22 kw. | c) Motor power HP=30, RPM= 1450, Hz=50, V=400 and 22 kw. | c) Motor power HP=30, RPM= 1450, Hz=50, V=400 and 22 kw. | c) Motor power HP=30, RPM= 1450, Hz=50, V=400 and 22 kw. | [5 empty] | c) Motor power HP=30, RPM= 1450, Hz=50, V=400 and 22 kw. | c) Motor power HP=30, RPM= 1450, Hz=50, V=400 and 22 kw. | c) Motor power HP=30, RPM= 1450, Hz=50, V=400 and 22 kw. | c) Motor power HP=30, RPM= 1450, Hz=50, V=400 and 22 kw.
| d) Protection: IP68 | d) Protection: IP55 | d) Protection: IP55 | d) Protection: IP55 | d) Protection: IP55 | [5 empty] | d) Protection: IP55 | d) Protection: IP55 | d) Protection: IP55 | d) Protection: IP55
A-2 | High lift station: |  |  |  |  | منظومة الدفع :
A-2-1 | High lift pump: Supply, install, connect, test and operate new heavy-duty high-lift pumping system, guaranteed for at least one year of operation (similar to Cabrari type or equivalent) with specifications as the following below: |  |  |  |  | مضخة الدفع: تجهيز وتركيب وتوصيل واختبار وتشغيل نظام ضخ جديد عالي الرفع للخدمة الثقيلة ، مضمون لمدة عام واحد على الأقل من التشغيل (على غرار نوع Cabrari أو ما يعادله) بمواصفات على النحو التالي:
| a) Pump discharge: Q=200 m3/h, H= 60 m at optimum functionality (due point) |  |  |  |  | تصريف المضخة: H=(60) m ,Q=200 m3/h, عند الأداء الأمثل (نقطة الاستحقاق) | No | 1
| b) Motor power: 55 KW, (1450-1500) RPM, 50Hz, 380V and IP:55 |  |  |  |  | قدرة المحرك: 55KW, (1450-1500) RPM, 50Hz, 380V and IP:55
| c) Bronze impeller, stainless steel shaft |  |  |  |  | الخنزيرة مصنوعة من البرونز ، الشفت عمود الفولاذ المقاوم للصدأ
| d) Insulation: class F |  |  |  |  | العزل: الفئة F
| The pump and electric motor drive shall be directly coupled to form a one horizontal unit fixed on a new concrete foundation (according to Anbar DoW tech. specifications) with making all the necessary work to fix the pump rigidly with deviation, with replacing the pipe from the collection basin to the pumps (1M for each pump), also, the work includes supply and install all the electrical cables connections (3×35mm2 +16 mm2 reinforced) with length 25 m from the electrical Board to the motor with all requirements (Tray cable, glands, terminals, etc...), the price includes transportation, installation, operation and providing all the needed materials and labours to implement the work correctly and successfully. |  |  |  |  | يجب أن تقترن المضخة والمحرك الكهربائي (كوبلن) مباشرة وتشكل وحدة أفقية واحدة مثبتة على لوح خرساني مسلح جديد (حسب المواصفات الفنية لمديرية ماء محافظة الانبار ) مع القيام بجميع الأعمال اللازمة لتثبيت المضخة بدون انحراف ، ويشمل العمل استبدال الانبوب من حوض التجميع الى المضخات ( و بطول 1م لكل مضخة) كما يشمل العمل تجهيز وتركيب جميع توصيلات الكابلات الكهربائية (مسلح 3 × 35 ملم2 + 16ملم2) بطول 25 متر من لوحة تحكم الكهربائية إلى المحرك مع جميع المستلزمات (كابل تري ، السدادات ، تيرمنال ، إلخ)، السعر يشمل النقل والتركيب والتشغيل وتوفير جميع المواد والعمالة اللازمة لتنفيذ العمل بشكل صحيح وناجح وحسب توجيهات المهندس المشرف.
A-2-2 | High lift pump (200 m3/h): Supply, install, connect, test, and operate a new heavy-duty high-lift pumping system (without electrical motor, Just Mechanical Pump), guaranteed for at least one year of operation (good quality) with specifications as the following below: |  |  |  |  | مضخة الدفع (الخنزيرة فقط) (200 م3/ساعة): تجهيز وتنصيب وتوصيل واختبار مضخة أفقية جديدة (الجزء المياكنيكي فقط بدون الماطور الكهربائي) (للخدمة الثقيلة) مضمونة لمدة عام على الأقل من التشغيل (نوعية جيدة )، والمواصفات على النحو التالي:
| a) Pump discharge: Q=200 m3/h, H=(60) m |  |  |  |  | تصريف المضخة: Q=200 m3/h, H=(60) m | No | 1
| b) Mecanical Pump power: 55KW, 1500) RPM, 50Hz,400V and IP:55 |  |  |  |  | قدرة المضخة الميكانيكية: 55KW, (1500) RPM, 50Hz, 400V and IP:55
| c) Bronze impeller, stainless steel shaft |  |  |  |  | الخنزيرة مصنوعة من البرونز ، الشفت عمود الفولاذ المقاوم للصدأ
| d) Insulation: class F |  |  |  |  | العزل: الفئة F
| The work includes lifting the effective pump and delivering it to the responsible party. The pump and the electric motor (Coplin) must be connected directly and form one horizontal unit installed on a concrete surface with all the work necessary to install the (NEW mechanical pump) with the electric motor without deviation. while ensuring that the work is completed correctly. |  |  |  |  | يشمل العمل رفع المضخة غير الفعالة وتسليمها للجهة المسؤولة. يجب ربط المضخة والماطور الكهربائي (كوبلين) مباشرة وتشكيل وحدة أفقية واحدة مثبتة عل ىسطح خرساني مع جميع الأعمال اللازمة لتركيب المضخة الميكانيكية مع الماطور الكهربائي دون انحراف . مع ضمان اتمام العمل بصورة صحيحة وحسب توجيهات المهندس المشرف.
A-3 | Non-return valves: |  |  |  |  | صمام مانع رجوع:
A-3-1 | Supply, install, connect and operate a new high-performance metal non-return valve, (stainless steel disc, swing check). The work includes providing all the required materials, accessories (flanges, rubber, bolts…etc.), tools and labor to complete the work properly and neatly as below: |  |  |  |  | تجهيز وتنصيب وربط وتشغيل صمام مانع رجوع جديد عالي الاداء من المعدن (قرص من الفولاذ المقاوم للصدأ, swing check) يشمل العمل توفير جميع المواد المطلوبة والملحقات (فلنجات, براغي ,واشرات مطاط,.....الخ) والأدوات والعمال لإكمال العمل بشكل صحيح وبدقة كما يلي:
| A- Non-return valve PN16 of size 150 mm 6 inches |  |  |  |  | صمام مانع رجوع PN16 حجم 150 ملم (6 انج) | No. | 4
| A- Non-return valve PN16 of size 200 mm 8 inches |  |  |  |  | صمام مانع رجوع PN16 حجم 200 ملم (8 انج) | No. | 2
A-4 | Ruber expansion joint: |  |  |  |  | مفصل تمدد مطاطي:
A-4-1 | Ruber expansion joint: Supply materials, tools and manpower to install new flexible joint for high lift pumps, The work includes providing all the required materials, accessories of flange adapter and rubber washers to complete the work properly and neatly as below: |  |  |  |  | مفصل تمدد مطاطي: تجهيز المواد و المعدات و الايدي العاملة لنصب فلكسبل جوينت لمضخات الدفع . العمل يشمل تجهيز كل المواد الضرورية و الملحقات و الفلنجات و الواشرات المطاطية لاكمال العمل بشكل صحيح كما يلي:
| a- Flexible joint PN16 of size 150 mm 6 inches |  |  |  |  | مفصل تمدد PN16 حجم 150 ملم (6 انج) | No. | 5
| a- Flexible joint PN16 of size 200 mm 8 inches |  |  |  |  | مفصل تمدد PN16 حجم 200 ملم (8 انج) | No. | 1
| a- Flexible joint PN16 of size 250 mm 10 inches |  |  |  |  | مفصل تمدد PN16 حجم 250 ملم (10 انج) | No. | 1
A-5 | Water Supply Meters: |  |  |  |  | عداد حساب كميات و ضغط المياه:
| Water Supply measuring devices: Provision of devices, equipment, and manpower to replace and install a new water pressure meter and flow meter to calculate the quantities of supplied water with all necessary equipment to be compatable with the system, including the below: |  |  |  |  | عداد حساب كميات و ضغط المياه: تجهيز المواد والقوى العاملة لاستبدال وتركيب عداد ضغط مياه جديد للنظام وتجهيز عداد اخر لحساب كميات الماء المجهز على تالنحو التالي:
A-5-1 | A- Water pressure gauge device, mechanical type, unit of measurement (bar/psi), (0 - 20 bar) |  |  |  |  | مقياس ضغط المياه . عداد يستخدم وحدة قياس( بار / بي اس اي), (0 - 20 بار) المنشأ ذو نوعية جيدة وحسب المواصفات المطلوبة | No. | 2
A-5-2 | B- Water supply quantity meter device, unit of measurement liter per hour |  |  |  |  | مقياس كمية إمدادات المياه ، 1 عداد يستخدم وحدة قياس / لتر ساعة | No. | 1
A-6 | Install columns: |  |  |  |  | تثبيت الاعمدة الحاملة الانابيب :
A-6-1 | Install columns: Supply materials and manpower to install the columns that carry the water pipe on the floor of the existing concrete station and replace the column base plate with an steel base plate thickness of 10 mm with dimensions of 30 * 30 cm The price includes all welding, painting, fixing and attaching the column base plate to the ground with (8) rot bolts of 18 mm diameter for each column base plate and brackets for pipe supports and fixing systems. To ensure that the shaft is properly fixed and balanced with the pipe Note: The columns and concrete bases are present and the work includes only the installation of the columns with all the work required to complete the work, As directed by the supervisor engineer |  |  |  |  | تثبيت الاعمدة الحاملة الانابيب : تجهيز مواد وقوى عاملة لتركيب الأعمدة التي تحمل ماسورة المياه على أرضية المحطة الخرسانية الحالية واستبدال صفيحة قاعدة العمود بقاعدة فولاذية سماكة 10 مم بأبعاد( سم30 * 30 ) السعر يشمل جميع اللحامات والطلاء ، تثبيت وربط صفيحة قاعدة العمود بالأرض بواسطة (8) مسامير دوارة بقطر 18 مم لكل لوح قاعدة عمود وكتيفة لدعامات المواسير وأنظمة التثبيت. للتأكد من أن العمود مثبت بشكل صحيح ومتوازن مع الأنبوب ملحوظة: الاعمدة والقواعد الخرسانية موجودة والعمل يشمل فقط تركيب الاعمدة مع كل الاعمال المطلوبة لانجاز العمل حسب توجيهات المهندس المشرف | Ls | 2
B | Electrical Works: |  |  |  |  | الاعمال الكهربائية :
B-1 | Electrical control board for Pump (200 m3/h): Maintenance of the main electrical control panel for a water station. It includes all the necessary electrical components and devices to ensure proper functionality and protection of the pump, The price includes maintenance or replacement of the damaged electrical parts of the main and secondary electrical board system (plunger) and supplying all the electrical equipment required by the system such as (phase filler, overload, three-phase 150 amp circuit breakers, 150 Amp three-phase contactor, timer, voltmeter, ammeter, Light bulbs, on and off buttons with the keys, phase scones with all required electrical connections) All components shall be properly installed and all electrical components of the panel shall be in compliance with the technical specifications and directions of the supervising engineer.. |  |  |  |  | الاعمال الكهربائية لمضخة (200 م3/ساعة): صيانة لوحة تحكم الكهربائية الرئيسية لمحطة ماء .يتضمن جميع المكونات والأجهزة الكهربائية الضرورية لضمان الأداء الوظيفي المناسب للمضخة وحمايتها ، ويشمل السعر صيانة أواستبدال القطع الكهربائية التالفة من منظومة البورد الكهربائي الرئيسية والثانوية (الغطاس) وتجهيز كل ماتتطلبه المنظومة من معدات كهربائية مثل(فيز فلر, اوفر لود, قواطع كهربائية سعة 150امبير ثلاثي الاطوار, كونتكتور سعة 150امبير ثلاثي الاطوار , مؤقت, فولتميتر, اميتر, مصبابيح ضوئية, ازرار تشغيل واطفاء مع المفاتيح , فيز سكونز مع كافة التوصيلات الكهربائية المطلوبة) يجب تركيب جميع المكونات بشكل صحيح وأن تكون جميع المكونات الكهربائية للوحة متوافقة حسب المواصفات الفنية و توجيهات المهندس المشرف. | Ls | 1
C-1 | Sedimentation tanks: |  |  |  |  | حوض الترسيب:
C1-1 | Sedimentation tanks: Providing materials, tools and manpower to clean and maintain the main steel sedimentation tank with dimensions (12.0 x 2.1 x 2.1) m, and the secondary with dimensions (1.9 * 2.0 * 3.5) m and welding procedure (welding carbon steel BS 2971) to ensure that there is no leakage And run the entire drainage system. Work includes completely removing mud and debris and making sure all drain holes are clean and functional. And cleaning the inner surface using the Sand Plast device, wiping and removing all residues on the surfaces and coating the inner surface with two layers of epoxy as the main and then three layers of epoxy for drinking water (food epoxy paint). The work includes dyeing with greasy paint from the outside, as well as replacing the damaged locks for the water drainage holes (butterfly lock 6 inches) according to the technical specifications and the directions of the supervising engineer. |  |  |  |  | احواض الترسيب: تجهيز المواد والأدوات و الايدي العاملة لتنظيف وصيانة خزان الترسيب الفولاذي الرئيسي ذي الأبعاد (12.0 × 2.1 × 2.1) م ، والثانوي ذو ابعاد (1.9*2.0*3.5)م وإجراء اللحام (لحام الفولاذ الكربوني BS 2971) لضمان عدم وجود تسرب وتشغيل نظام الصرف بالكامل. يشمل العمل إزالة الطين والمخلفات تمامًا والتأكد من نظافة جميع فتحات التصريف ووظيفتها. و تنظيف السطح الداخلي باستخدام جهاز ساند بلاست ، و مسح و ازالة جميع المخلفات الموجودة على الأسطح و طلاء السطح الداخلي بطبقتين من الإيبوكسي كرئيسي ثم ثلاثة طبقات من الإيبوكسي الخاص بمياه الشرب (طلاء إيبوكسي غذائي) . يشمل العمل اعمال الصبغ بالطلاء الدهني من الخارج و كذلك استبدال الاقفال التالفة الخاصة بفتحات تصريف الماء (قفل فراشة 6 انج) و حسب المواصفات الفنية و توجيهات المهندس المشرف | Ls | 2
C-2 | Rehabilitation of Sand Filters |  |  |  |  | إعادة تأهيل المرشحات الرملية:
C-2-1 | Rehabilitation of Sand Filters: Rehabilitation of cylindrical sand filters with dimensions of (Dia. 2.0m x L 6.5m) of the compact unit, including replacement the media of the filters (gravel and sand) and maintaining it through treating leakage areas and removing the rust in a proper way by using Angle Grinder or sand, and lining from inside by non-toxic epoxy (2 layers) and oil paint from outside (2 layers) with all connection pipes (inlet and outlet) and the steel structure of filters, the price includes source protection by cleaning the intake and collection tank, with construction and installation of antirust steel screen gate with its holes not greater than 4x4cm, and construction with installation of an iron cover for the intake source with any necessary work and providing materials for this works, the price also includes maintaining all the valves and replacement of non-functional nozzles (if any), and re-filling filters with new gravel and sand and according to the technical specifications of the filters with a thickness of not less than (90) cm as below: A. Gravel size (9.5-13) mm thickness (10) cm. B. Gravel size (6.5-9.5) mm thickness (10) cm. C. Gravel Size (2.5-6.5) mm thickness (10) Ctn. D. Effective size of sand (0.6-0.65) mm thickness (60) cm and the coefficient of regularity does not exceed (1.5)All components must be installed correctly and all components must be in accordance with the technical specifications and directions of the supervising engineer. |  |  |  |  | إعادة تأهيل المرشحات الرملية الأسطوانية بأبعاد (قطر 2.0 م × اطول 6.5 م) للوحدة المجمعة بما في ذلك استبدال وسائط الفلاتر (الحصى والرمل) وصيانتها من خلال معالجة مناطق التسرب وإزالة الصدأ بطريقة مناسبة عن طريق باستخدام كوسره اليدوية أو الرمل ، والتبطين من الداخل بإيبوكسي غير سام (طبقتان) وطلاء زيتي من الخارج (طبقتان) مع جميع مواسير التوصيل (مدخل ومخرج) والهيكل الفولاذي للفلاتر ، السعر يشمل حماية المصدر عن طريق تنظيف خزان السحب والتجميع ، مع إنشاء وتركيب بوابة من الفولاذ المقاوم للصدأ بفتحات لا تزيد عن 4 × 4 سم ، والبناء مع تركيب غطاء حديدي لمصدر السحب مع أي أعمال لازمة وتوفير المواد لهذه الأعمال ، السعر أيضا يشمل صيانة جميع الصمامات والاقفال واستبدال نوزلات غير افعالة (إن وجدت) ، وإعادة تعبئة الفلاتر بالحصى والرمل الجديد وحسب المواصفات الفنية للفلاتر بسمك لا يقل عن (90) سم كالاتي: أ. الحصى مقاس (9.5-13) ملم بسمك (10) سم. ب- الحصى مقاس (6.5-9.5) مم سماكة (10) سم. ج- الحصى حجم (2.5-6.5) مم سماكة (10) قيراط. د- الحجم الفعال للرمل (0.6 - 0.65) ملم بسمك (60) سم ومعامل الانتظام لا يتجاوز (1.5).يجب تركيب جميع المكونات بشكل صحيح وأن تكون جميع المكونات متوافقة حسب المواصفات الفنية و توجيهات المهندس المشرف. | Set | 1
C-3 | Chlorine & Alum Feed System |  |  |  |  | أنظمة الكلور والشب
C3-1 | Supply, install, connect, to maintenance, and commission Chlorine & Alum Feed System guaranteed for at least one year of operation (good quality) which the supervisory committee should approve before starting supplying process, and consist of three polyethylene tanks of 1000 Lit capacity (for each tank), two mixers with stainless steel shaft and impeller which should be installed at the top of each tank with electric motors of speed 900 rpm, IP 55, class F, 220 V / 50 Hz/ power 1,50 KW, two dosing pumps of 300 l/hr. capacity and head not less than 0. 8 bar, power 0,37 KW, speed 1370 rpm, IP 55, Inlet / Outlet Connections: (3/4"), the work includes gages, all electrical and mechanical installation, and connection accessories, with all the works required to complete the job. Certificates of origin and inspection documents are required, as directed by the supervising engineer. |  |  |  |  | تجهيز وتركيب وربط لصيانة وتشغيل نظام تغذية الكلور والشب مضمون لمدة عام واحد على الأقل من التشغيل (جودة جيدة), والتي يجب أن توافق عليها لجنة الإشراف قبل البدء في عملية التوريد ، وتتكون من ثلاثة خزانات بولي إيثيلين بسعة 1000 لتر (لكل خزان) ، وخلاطين بعمود من الفولاذ المقاوم للصدأ ومكره (دافع) يجب أن تكون مثبتة في الجزء العلوي من كل خزان بمحركات كهربائية بسرعة 900 دورة في الدقيقة ، IP 55 ، فئة F ، 220 فولت / 50 هرتز / قوة 1،50 كيلوواط ، مضختان للجرعات 300 لتر / ساعة. السعة والرأس لا تقل عن 0. 8 بار ، الطاقة 0.37 كيلوواط ، السرعة 1370 دورة في الدقيقة ، IP 55 ، وصلات المدخل / المخرج: (3/4") ، العمل يشمل العدادات ، جميع التركيبات الكهربائية والميكانيكية ، والتوصيل الملحقات ، مع كافة الأعمال المطلوبة لإتمام المهمة. مطلوب شهادات منشأ ووثائق فحص وحسب توجيهات المهندس المشرف. | Ls | 1
D | Excavation works and laying pipes |  |  |  |  | أعمال الحفريات ومد انابيب
| PVC Pipe provision for water supply : Supply, installation, connection, and testing of PVC pipes with a diameter as mentioned below and at least 10 bar air pressure and a connection with a pipe PVC, provided that the provided trademark conforms to the Iraqi specifications and is approved by the Supervisory Committee with all accessories and subject to all necessary laboratory tests before using it. It includes digging a pipeline trench in any type of soil with a depth of at least 110 cm and a width of 60 cm, spreading a layer of river sand 30 cm thick around the pipe, removing all excavation materials at the site, removing and cleaning the pipeline alignment from the water Overhanging, pulling plastic pipes inside the steel pipe with a diameter of 250 mm and a thickness of 5 mm in areas that intersect with irrigation channels, roads and drainage inconsistent with the path of the pipeline, placing a warning tape along the pipe path, all fittings and accessories, elbows, tees, valves, reducers, couplings, flanges, washers..etc. The work includes making concrete bolster for elbows and connections and connecting the new water network with the existing one with all sublines and leveling the ground as it was before the work and lifting the debris and throwing it out of the municipality's borders according to the specifications and directions of the supervising engineer. as the following below: |  |  |  |  | أنبوب PVC : تجهيز وتركيب وربط واختبار انابيب PVC بقطر كما مطلوب ادناه, وان لايقل عن ضغط جوي 10 بار وايصاله مع وانبوب على ان تكون العلامة التجارية المقدمة مطابقة للمواصفات العراقية ومعتمدة من قبل لجنة الاشراف مع كافة الملحقات واخضاعها لكافة الفحوصات المختبرية اللازمة قبل استخدامها. يشمل حفر خندق خط الأنابيب في أي نوع من أنواع التربة بعمق لا يقل عن 110 سم وعرض 60 سم ، ونشر طبقة رمل نهرية بسمك 30 سم حول الأنبوب ، وإزالة جميع مواد الحفر في الموقع المعتمد من قبل السلطات المحلية ، وإزالة وتنظيف محاذاة خطوط الأنابيب من المياه المتراكمة ، وسحب الأنابيب البلاستيكية داخل الأنبوب الفولاذي بقطر 250 مم وسمك 5 مم في المناطق التي تتقاطع مع قنوات الري والطرق والصرف غير المتسقة مع مسار خط الأنابيب ، ووضع شريط تحذير على طول مسار الأنابيب ، جميع التركيبات والإكسسوارات ،و الأكواع ، الصمامات ، صمامات الفحص ، المخفضات ، الوصلات ، الفلنجات ، الواشرات إلخ.يشمل العمل عمل دعامة خرسانية للأكواع والتوصيلات وربط شبكة المياه الجديدة بالشبكة القائمة بكافة الخطوط الفرعية وتسوية الارض كما كانت قبل العمل ورفع الركام ورميها خارج حدود البلدية حسب المواصفات و توجيهات المهندس المشرف. على النحو التالي:
D-1 | A-PVC pipe size 225 mm (8) inches |  |  |  |  | أنبوب PVC مقاس 225 ملم (8) انج | ml | 700
D-2 | B-PVC pipe size 150 mm (6) inchies |  |  |  |  | أنبوب PVC مقاس 150 ملم (6) انج | ml | 1200
D-3 | B-PVC pipe size 100 mm (4) inchies |  |  |  |  | أنبوب PVC مقاس 100 ملم (4) انج | ml | 500
Sub-total
Any other costs (please specify)
Total Price
Requested by DRC | [6 empty] | Bidder to Fill
Delivery time required (days after the site handover): | [5 empty] | 30 calendar days | Delivery time offered (days after the site handover):
Delivery Terms required (Add Incoterm if necessary): | [5 empty] | DDP INCOTERMS 2020 | Delivery time offered (days after the site handover):
Delivery Destination required: | [5 empty] | Ameriat Al Fallujah in Anbar district | Delivery Destination offered:
Minimum bid validity period required: | [5 empty] | 90 Days | Bid validity period offfered:
Currency of Tender: | [5 empty] | USD Only | Currency of Bid:
Company Name:
Signed by a duly authorized company representative:
Title:
Date:
Print Name:
Stamp of company
Note on J5: Author: Latitiude
Note on K5: Author: Longitude
Note on I32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2
Note on I33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: no need
Note on I34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: no need
Note on B36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Dhuha Mezher Abdulqader this is confusing! is it pressure meter/switch or flow meter? Reply: measuring devices
Note on B37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Dhuha Mezher Abdulqader better to add range min-max (Bar/PSI)
Note on I37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4 including filters
Note on B38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Dhuha Mezher Abdulqader ultrasonic flow meter https://www.industry-plaza.com/ultrasonic-flowmeter-proline-prosonic-p61749498.html Reply: it will be high suphticated, I don't think DoW have the ability to deal with
Note on B40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The columns already exist, only fixing on the ground is needed
Note on B42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Dhuha Mezher Abdulqader I recommend being more specific on what should be changed/replaced. normally, better to replace the board, or at lease replace all contactors and circuit breakers with new ones and keep the existing ones as spare
Note on I42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: only one main board
Note on I46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 14 m3
Note on B50: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Dhuha Mezher Abdulqader I do understand that this is because its raw water, but DoW don't use PVC anymore and they changed the existing ones to Polyethylene in recent years