## Sheet1
Annex K1 Provision of clean drinking water in Basra City- ZONE 6
ITEM | DESCRIPTION
|  | QTY | UNIT | Unit Cost USD | Total Cost USD
Works of Garma 1
1 | Supply, install and operate horizontal set split case pumps (pump, elect. Motor, star delta starter) with flow rate capacity of 1000m3/hr. & head of 80m.form west origins such as KSB-Germany, Grundfos-Hungary, Grundfos-Denmark, and Willo-Germany. The pump shall comply with the standard specifications. - Supplying all materials and accessories for the connection (all pipes that are used on both sides of the intake and delivery of the pumps and made of carbon steel, the thickness of which is not less than 10 mm) with the provision of all the accessories necessary for the connection such as elbow, TEE, and reducers with cutting and welding works the work include supply and install of gearbox valves, non-return and anti-vibration on both sides of the pump and the valve should provide form of the origins approved by the Basra Water Directorate (English, French, German, Belgian, American, Japanese) in addition to the work of the header - The diameter of all accessories form suction side shall be at least 100 mm larger than the pump section flange and Delivery side accessories diameter 100 mm larger than the pump delivery flange Pump Specifications IP-55, F-type insulation Impeller type: S Bronze Shaft type: S.S. 420 Pump Efficiency: not less than 75% Pump case outside coating: powder coating Pump case inside coating: epoxy coating Pump casing: ductile iron or cast iron Drive type: electric motor with VFD drive Motor voltage: 380 volts Motor power: not less than 360 kW The price is also all the requirements for installing the pumps on new concrete bases as an alternative to the old concrete bases that are compatible with the new pumps, and preparing all materials and tools for installing screws, nuts, weight and calibration indicators, as well as electrical connection and everything that the work requires | 2 | No. |  | 0
| Total |  |  |  | 0