## BoQ acronyms
BRC = Bar Reinforced Concrete.
SBR = styrene butadiene rubber.
NP = Nominal pressure.
GGG50 = This is the code of the materials that the item made from it.
HT = high tension.
LT = low tension.
ST = steel type
ACSR = Aluminum conductor steel-reinforced cable.
LDPI = Ligh-Density Polyethylene pipe.

## General guidness
General Guidelines
1 | All works and the materials supplied by the contractor must be in according with the relevant Iraq's standard Specifications ( It’s the contractor responsibility to obtain any relevant Iraqi specifications by visiting ministry of construction and housing web site: www.moch.gov.iq (or physically obtain those documents from the mentioned ministry) in addition to Iraqi technical specification for building works, with considering the USAID guidelines .
2 | The contractor must provide samples, catalogues for testing / inspection and approval by the site engineer.
3 | Contractor must pay the cost for samples including any laboratory tests, both inside and outside the country as required.
4 | The price of works includes all job requirements as per Iraq's standard specification.
5 | The contractor must provide PPE for all laborer's, personnel, engineers and possible visitors to the site.
6 | Design plans and BoQ are complementary to each other, hence the contractor has the obligation to execute the tasks mentioned in both of them. accordingly The contractor's shall include all what is mentioned in the drawings & all what is mentioned in the BOQs. Incase BOQ and technical drawings have discrepancies. BOQ supersedes technical drawings. Follow Taafi site engineers instruction at all times.
7 | All the BoQ articles comprise supplying manpower, machinery, equipment, transportation all necessary requirements to get the work done properly regardless of it's mentioned in the BoQ articles or not.
8 | In case that there is any item or detail in the drawings not mentioend in the BOQ (or vise versa) then this item or detail is considered included in the contractor's price for this project & he should execute it within his contract price without claiming any increase to the contract price, as it is considered part of the contract.
9 | All the BoQ articles, and Drawings must be carried out according to guidelines of Iraqi Technical Specifications with updates and instructions of Taafi site engineers.
10 | All the BoQ articles comprise removing and transporting any debris or rubble to allocated disposal areas by municipality or local authority.
11 | Site visit is MANDOTORY (unless its mentioned OPTIONAL) for contractors prior to bid proposal. Submit site letter of undertaking for the project with cost proposal, mentioning site been visited with tendering documents.
12 | Follow Taafi site engineers instruction at all times.
13 | Taafi engineers has the authority to revise any changes or configurations of construction works upon site condition with coordination with Taafi managements , with no added cost to construction.
14 | The price includes all required materials, machines and instruments, labor works and all the requirements stated in the contract items and design drawings and details. as well as all necessary accessories to complete the work in all aspects. including Suppllying materials and all required fittings , accessories , tools and machine , installating , testing and comessioning and put in operation to get the system work properlly as per international specifications , beneficiary and Taafi engineer instructions.
15 | Any damaged parts in any system or structure due to the work in the site , will be responsibility of contractor to redo poor workmanship without cost to Taafi .
16 | The contractor shall check all items and measurements given in the BoQ. All changes, additional quantities etc. require the written approval by the project engineer. A site assessment by the contractor is mandatory.
17 | All supplied materials and products should be as specified below ( Same Brands , model and origin ). Show sample for project engineer approval before procurement and installation.
18 | Curing for all concrete works should be not less than 7 days before construction start above any conctrete structure
19 | Cleaning and waste management of work site should me on daily basis with environmental friendly and healhy way.
20 | All materials and accessories to be used are new and of origin and brands known, and the contractor to prepare samples for approval before the start of work and use.
21 | Please, read all the documents carefully, then price it.

## Civil Works
CIVIL WORKS
# | Item Description | Unit | Qty | Price $
Site work
1 | Site preparation-Heavy Cleanin site: Supply of materials, tools, machineries and manpower for site preparation. The work includes: 1-Clearing, stripping and levelling of the site. 2-Removing undesired plants and other natural vegetation. 3-Removing all the damaged roofing layers, slabs, walls, fences, finishing materials, flooring tiles, tile bedding, etc. 4-Dumping of all the debris and rubble to a site approved by the local authorities. All needed work to complete the job will be included within the price. | m² | 1
2 | Site preparation-Medium Cleaning site: Supply of materials, tools, machineries and manpower for site preparation. The work includes: 1-Removing the surface layer of soil in site about 20 cm thickness and Clearing, stripping and levelling of the site. 2-Removing undesired plants and other natural vegetation. 3-Dumping of all the rubble of cutting soil to a site approved by the local authorities. All needed work to complete the job will be included within the price. | m² | 1
3 | Site preparation- light clean site: Supply of materials, tools, machineries and manpower for site preparation. The work includes : 1-Cleaning the site from light debris, scattered stones, undesired plants and other Organic materials, destroyed furniture, dust and soil on the floors. 2-Dumping of all the rubble of cleaning site to a site approved by the local authorities. All needed work to complete the job will be included within the price. | m² | 1
4 | Site preparation-Cutting/Trimming the Edges of the Patches(Potholes/Ruts): Supply of materials, tools, machineries and manpower to cut/trim the edges of the patches (potholes/ruts) in regular shapes using asphalt saw cutting machine as following: 1-Cutting/trimming the sides of the existing asphalt surface to provide firm vertical faces. 2-Removing all the damaged asphalt layers and corrugated asphalt surfaces. 3-Removing all rubble and debris to a dump site approved by the local authorities. 4-All the needed works to complete the job shall be included within the price. All works should be according to the technical specifications for roads. | m² | 1
5 | Demolishing works: Supply of materials, tools and manpower to demolish the damaged parts (AS Example foundation, walls,slab,beam,column, old septic tankroofing layers, slabs, walls, fences, finishing materials, flooring tiles, tile bedding, etc.)and remove all the debris to a site approved by local authorities. All needed works to complete the job, will be included within the price". | m³ | 1
Excavation & Backfilling works
6 | Excavation works: Supply of materials, tools, machinery, and manpower for excavation to the required level of (25-100)cm. The works include leveling, transporting, loading, and unloading all surplus materials to a site approved by the local authority. All needed works to complete the job should be included within the cost. | m³ | 1
7 | Cutting the concrete and asphalt: Supply material, tools, machineries and manpower to cutting the concrete and asphalt from two sides, with thickness (10-15) cm, and width at least 50 cm for pipe lines and at least 1 m for the conction points places, with remove and transporting all resulted materials, debris and exist concrete to approved location by local authorities (Municipality). All needed works to complete will be include within the price and as directed and instruction by Ta'afi supervisor Enginee. | m.l | 1
8 | Path Excavation works: Supply material, tools, machineries and manpower to excavate all types of soil (hard, soft, and rocks), width at least 50 cm and depth at least 70 cm, with remove and transporting all resulted materials, debris and exist concrete to approved location by local authorities (Municipality). All needed works to complete will be include within the price and as directed and instruction by Ta'afi supervisor Engineer. | m.l | 1
9 | Backfilling works-subase: Supply of materials, tools, machinery, and manpower for backfilling, by using subbase materials from natural sources free from clay, silt, or any or organic materials. Backfilling material shall be applied on layers of (20-25) cm thickness, watered, and compacted to min 95% of MDD (Maximum density dryer). All needed works to complete the job should be included within the cost. | m³ | 1
10 | Backfilling works-Cobbles -: Supply of materials, tools, machinery, and manpower for backfilling by using Cobbles materials from natural sources clean free from limestone,clay and silt for make filter to pumping ground water. the size of Cobbles range (60-250mm) Backfilling material shall be applied on layers of (30-40) cm thickness, watered, and compacted by heavy machine . All needed works to complete the job should be included within the cost." | m³ | 1
11 | Backfilling works-subase riverine type plus cement: Supply of materials, tools, machinery, and manpower for backfilling, by using subase riverine materials from natural sources free from clay, silt, or any or organic materials. Backfilling material shall be applied on layers of (20-25) cm thickness mixed with 0.5% cement using sulphate resisting cement SRC, watered, and compacted to min 95% of MDD (Maximum density dryer). All needed works to complete the job should be included within the cost. | m³ | 1
12 | Spreading Gravel: Supply gravel and spread it on the ground, with a thickness of 7cm, length of the one gravel's piece between 1-3cm The works include: - Leveling and compacting the site after spreading the gravel - Doing all requirements to complete good work, according to the instruction by the Supervisor Engineer.All needed works to complete the job should be included within the cost. | m² | 1
Foundation
13 | Reinforced Concrete for foundation (40x60cm): Supply of materials, tools, and manpower for casting reinforced concrete for foundation (40x60cm) using concrete (C25MPa) and reinforcing steel 8-Ø12mm and rings Ø10mm @25cm C/C, with using the vibrate machine,using sulphate resisting cement SRC. The work includes all the requirements, concrete covers, formworks ,laying a sheet of polyethylene of 1mm thickness, leveling and concrete curing. The price include cleaning the bed of the excavation. All needed works to complete the job will be included within the price.SEE ATTACHED DRAWING #2. | m³ | 1
14 | Reinforced Concrete for foundation of Fence (30x50cm): Supply of materials, tools, and manpower for casting reinforced concrete for foundation (30x50cm) using concrete (C25MPa) and reinforcing steel 6-Ø12mm and rings Ø10mm @25cm C/C, with using the vibrate machine,using sulphate resisting cement SRC. The work includes all the requirements, concrete covers, formworks ,laying a sheet of polyethylene of 1mm thickness, leveling and concrete curing. The price include cleaning the bed of the excavation. All needed works to complete the job will be included within the price. | m³ | 1
15 | Reinforced Concrete for Raft foundation (LxW): Supply of materials, tools, and manpower for casting reinforced concrete for foundation (LxW) thickness 40cm using concrete (C25MPa) and reinforcing steel 12 mm@20cm C/C in two direction double layer and reinforcement the beams 8Ø12mm- for stirrups use Ø10@25cm C/C,the beams@space 4m in two direction and according to supervisor engineer, with using the vibrate machine,using sulphate resisting cement SRC. The work includes all the requirements, concrete covers, formworks ,laying a sheet of polyethylene of 1mm thickness, leveling and concrete curing. The price include cleaning the bed of the excavation. All needed works to complete the job will be included within the price.SEE ATTACHED DRAWING #1. | m³ | 1
Walls Constraction Work
16 | Masonry works above foundation (W40xH30)cm : Supply of materials, tools, and manpower to rebuild walls above foundation using solid concrete blocks (15x20x40) cm with width 40cm and height 30cm, with cement sand mortar (1:3). The wall should be levelled vertically and horizontally. All needed works to complete the job will be included within the price.SEE ATTACHED DRAWING #9. | m³ | 1
17 | Repair Wall-Reconstruction of Damaged ( Stone ) Walls(width 40cm): Supply of materials, tools and manpower to demolish the damaged parts of the walls and remove all the debris to a site approved by local authorities, then reconstruction using 25X20X15cm stone and cement mortar (1: 3) including flush pointing inside and outside of the walls with cement sand mortar (1:3). The price includes filling the space between the stones with plain concrete (C20MPa). The joints between stones should be according to specifications but not exceeds 4cm. All needed work to complete the job will be included within the price. | m³ | 1
18 | Repair Wall-Reconstruction of Damaged ( Block) Walls: Supply of materials, tools and manpower to demolish the damaged parts of the walls and remove all the debris to a site approved by local authorities, then reconstruction ( 20cm) of the walls using solid concrete block (15x20x40cm) with cement sand mortar . The wall should be levelled vertically and horizontally. All needed works to complete the job, will be included within the price | m³ | 1
19 | New-construction Wall by (solid concrete blocks): Supply of materials, tools and manpower for building walls, by using solid concrete blocks 15x20x40cm with width 20cm, with cement mortar (1:3) mix ratio. The wall should be leveled vertically and horizontally. The cost of the work shall include all the requirements to complete the job. | m² | 1
20 | New-construction Walls by Stone (width 40cm): Supply of materials, tools and manpower to construction the walls using 25X20X15cm stone and cement mortar (1: 3) including flush pointing inside and outside of the walls with cement sand mortar (1:3). The price includes filling the space between the stones with plain concrete (C20MPa). The joints between stones should be according to specifications but not exceeds 4cm. All needed work to complete the job will be included within the price. | m³ | 1
21 | New-construction of Retaining Wall by (solid concrete blocks): Supply of materials, tools and manpower for building walls, by using solid concrete blocks 15x20x40cm with width 40cm, with cement mortar (1:3) mix ratio. The wall should be leveled vertically and horizontally. The cost of the work shall include all the requirements to complete the job. | m³ | 1
22 | Brick works: Supply of materials, tools and manpower to rebuild walls, thickness of wall 24 cm, using brick (7.5*11.5*24cm) with cement sand mortar (1:3). The wall should be levelled vertically and horizontally. All needed works to complete the job will be included within the price. | m³ | 1
23 | Parapet-width 15cm: Supply of materials, tools and manpower to rebuild parapet wall with width 15cm using hollow concrete blocks 15x20x40 cm and sand mortar (1:3). The work includes the cement plastering for two sides and the upper of parapet. All needed works to complete the job will be included within the price. | m² | 1
24 | Masonry works (hollow concrete blocks): Supply of materials, tools and manpower for building walls, by using hollow concrete blocks 20x20x40cm, with using cement mortar (1:3) mix ratio. The wall should be leveled vertically and horizontally. The cost of the work shall include all the requirements to complete the job. | m³ | 1
25 | Glass Brick: Supply of materials, tools and manpower to remove the damaged glass brick and dump it to a site approved by local authority, then install new glass brick (Same texture, shape and size). The price includes filling all the gabs and joints by special sealant. All needed works to complete the job, will be included within the price. See attached annex. | m² | 1
26 | Clay Brick Works: Provision of materials, labour and equipment and all requirements to complete the works. Demolish the damaged parts of walls, remove all debris to a site approved by local authorities. Rebuild walls using clay brick, colour to match existing (7.5*11.5*24cm) using a cement sand mortar (1:3) only if existing wall uses similar. Mortar mix as follows: hydrated lime powder (1), sand (2) (river sand with small grains). The wall should be levelled vertically and horizontally, in accordance with supervising engineer instructions. | m³ | 1
27 | Ceiling Dome (New) Provision of materials, labour and equipment and all requirements to complete the works. Applicable to Cradle domes, Bakdasheya dome, Tisht domes and Jack arch dome (including supplying I steel beam and all accessories whenever needed). the work includes build with stone and lime mortar to match existing parts. Lime plaster to be applied based on the following mix ratio: Mortar mix as follows: hydrated lime powder (1), sand (2) (river sand with small grains). Price to include supporting of the dome and walls, where necessary. All works in accordance with supervising engineer instructions. | m³ | 1
28 | Ceiling Dome (Repair) Provision of materials, labour and equipment and all requirements to complete the works. Applicable to Cradle domes, Bakdasheya dome, Tisht domes and Jack arch dome (including supplying I steel beam and all accessories whenever needed). the work includes removing all the weak and damaged parts of the dome and rebuild with stone and lime mortar to match existing parts. the price includes stabilize and support all the unstable parts. All gypsum plaster to be removed and disposed of. Lime plaster to be applied based on the following mix ratio: Mortar mix as follows: hydrated lime powder (1), sand (2) (river sand with small grains). Price to include supporting of the dome and walls, where necessary. All works in accordance with supervising engineer instructions. | m³ | 1
Cast Concrete
29 | Reinforced Concrete slab, beam, lintel, staircase and parapet: Supply of materials, tools and manpower for casting reinforced concrete slab, beam, column, lintel, louver, parapet, decoration and staircase using concrete (C25MPa). The price includes adding bonding agent material between the old and new concrete(if any). The work includes all the requirements of steel reinforcement, concrete covers and formworks. All needed works to complete the job will be included within the price. Slab: Ø12mm @20cm c/c two layers and both directions. Beam: 3Ø12 top, 3Ø12 bottom and stirrups Ø10mm @20cm c/c. Stair: Ø12mm @ 20cm c/c two layers and both directions,parapet:Ø12mm @20cm C/C in two direction-one layer. SEE ATTACHED DRAWING #9. | m³ | 1
30 | Reinforced Concrete of Column: Supply of materials, tools and manpower for casting reinforced concrete, column using concrete (C-MPa). The price includes adding bonding agent material between the old and new concrete(if any). The work includes all the requirements of steel reinforcement, concrete covers and formworks. All needed works to complete the job will be included within the price.Column: 8Ø16mm and stirrups Ø10mm @20cm c/c. C25MPa)
a | C25Mpa | m³ | 1
b | C30Mpa | m³ | 1
31 | Reinforced Concrete for Single Column Footings: Supply of materials, tools and manpower for casting reinforced concrete single column footings using (C25MPa) concrete and using sulphate resistance cement. The work includes all the requirements of steel reinforcement, concrete covers and formworks(if required). All needed works to complete the job will be included within the price. See attached drawing#16. | m³ | 1
32 | Reinforced Concrete for Short Columns (Pedistals): Supply of materials, tools and manpower for casting reinforced concrete (60x60cm) short columns (pedistals) using (C25MPa) concrete and using sulphate resistance cement. The work includes all the requirements of steel reinforcement, concrete covers and formworks. All needed works to complete the job will be included within the price. See attached drawing#16. | m³ | 1
33 | Reinforced Concrete for Retaining Wall Supply of materials, tools and manpower for casting reinforced concrete (C25MPa) using sulphate resistance cement for foundations and ordinary Portland cement for walls. The work includes all the requirements of steel reinforcement, covers and formworks. All needed work to complete the job will be included within the price. SEE ATTACHED DRAWING #3.
a | C25Mpa | m³ | 1
b | C30Mpa | m³ | 1
34 | Repairing of Slab: Supply of materials, tools, machinery and manpower for repairing of reinforced concrete slab by demolition of the destroyed area of the slab and dumping of all debris and rubble to a site approved by local authorities. Price will include recasting a reinforced concrete 20cm thickness (or same as the existing) for the damaged area of the slab using concrete (C25MPa) , providing formwork, rebar Ø12mm@150mm both directions and top and bottom and using bonding agent (like SBR) to create a bonding slurry when mixed with cement. The new slab must rest on the old slab by a minimum distance not less than 50 cm and treat both contacted slab by isolated material to prevent water leakage. All needed works to complete the job, will be included within the price. | m² | 1
35 | Concrete with BRC: Supply of materials, tools and manpower for casting (15cm ) concrete with BRC(200x200x5mm) using sulphate resistant cement for (C-MPa) concrete. The price includes providing expansion joints every 4m both directions.The price includes adding bonding agent material between the old and new concrete(if any). The work includes all the requirements of concrete covers and formworks. All needed works to complete the job will be included within the price.NOTE: the final layer of the floor should be smooth by using a helicopter concrete finishing, also using the cutter to have a joint.
a | C20Mpa | m² | 1
b | C25Mpa | m² | 1
36 | Plain Concrete:- Supply of materials, tools and manpower for casting (10cm ) plain concrete (C-MPa) using sulphate resistance cement . The price includes adding bonding agent material between the old and new concrete(if any). The work includes all the requirements of concrete covers and formworks. All needed works to complete the job will be included within the price.NOTE: the final layer of the floor should be smooth by using a helicopter concrete finishing, also using the cutter to have a joint.
a | C15Mpa | m² | 1
b | C20Mpa | m² | 1
c | C25Mpa | m² | 1
37 | Reinforced Concrete Floor(Slab on Grade): Supply of materials, tools and manpower to cast reinforced concrete (C-MPa) for floors, 20 cm thickness using sulphate resistant cement. The work includes laying Ø10mm @20cm c/c (@ mid height) in both direction and providing expansion joints every 5m both directions. The work includes all the requirements, concrete covers, formworks ,laying a sheet of polyethylene of 1mm thickness, leveling and concrete curing. All needed work to complete the job will be included within the price.NOTE: the final layer of the floor should be smooth by using a helicopter concrete finishing, also using the cutter to have a joint.
a | C20Mpa | m² | 1
b | C25Mpa | m² | 1
38 | Reinforced concrete base for Generator(W ×L mx20 cm thickness) : Supply of materials, tools and manpower to cast concrete for generator base. Including demolishing the damaged concrete base and removing and dumping of rubble to a site approved by local authorities, excavation soil 20 cm depth, backfilling with sub-base materials 20 cm thickness, proper compactation 90%, fomworks, polyethylene sheet laying 1mm thick, casting concrete (C21Mpa) of 20 cm thickness reinforced by one layer of welded mesh wire (BRC Ø4mm 15x15cm), apply expansion joints every 4m in both directions, leveling, smoothing, testing and curing. All needed works to complete the job will be included within the price. | m² | 1
39 | Stamp Concrete: Provide all the machines, materials, and workforce required to cast colored stamp concrete(C-MPa) 15cm with a layer of BRC(200x200x5mm) the running track and the walkways. The work includes all the requirements, concrete covers, formworks ,laying a sheet of polyethylene of 1mm thickness, leveling and concrete curing. All needed works to complete the job will be included within the price.NOTE: using the cutter to have a joint. | m² | 1
a | C20Mpa | m² | 1
b | C25Mpa | m² | 1
40 | Cast concrete for floors with high Load : Supply of materials, tools and manpower to cast plain concrete (C), of compressive strength as defined by standard 150mm cube at 28 days shall be 25 N/mm², using sulphate resisting cement SRC, including reinforced in both directions Including horizontal and vertical levelling, formwork, admixtures, curing, all necessary fixing, fittings and all required as per drawings, specifications and the Engineer's approval. All needed works to complete the job should be included within the cost.
a | C25Mpa-reinforced by Ø12mm@15cm c/c | m³ | 1
b | C30Mpa-reinforced by Ø16mm@15cm c/c | m³ | 1
Plastering
41 | New Gypsum Plastering : Supply of materials, tools and manpower for gypsum plastering with 20mm thickness smooth-finished for walls and ceilings using aluminum straight edges. The price includes one layer of cement splash dash under gypsum plastering with cement-sand mortar. All needed works to complete the job will be included within the price. | m² | 1
42 | Gypsum plastering with crack repairing: Supply of all necessary materials, tools and manpower to remove the damaged gypsum plastering of walls & ceiling and plastering with new gypsum plastering in 2 layers minimum thickness 20mm.The work includes repairing of wall cracks by removing the damaged gypsum plastering 25cm at each side of the crack, then filling the cracks with cement mortar 1:3 and using SBR at a rate of 50gr per m2 , later putting a layer of plastic mesh on the area under the gypsum plastering. All needed works to complete the job, will be included within the price. | m² | 1
43 | Gypsum Plastering without crack repairing: Supply of materials, tools and manpower to remove the damaged gypsum plastering parts of ceilings and internal walls. The work includes remove the damaged parts and cracks of old plaster layers and re-plastering with 20mm thickness smooth-finished for internal walls and ceilings using aluminum straight edges. The price includes one layer of cement splash dash under gypsum plastering with cement-sand mortar. All needed works to complete the job will be included within the price. | m² | 1
44 | New Cement Plastering : Supply of materials, tools and manpower for cement plastering with 20mm thickness smooth-finished for walls and fences walls using aluminum straight edges. The price includes three layers as follows: one layer of cement splash dash, one layer of rough (kafmal) and finally smooth finished cement plastering with cement-sand mortar. All needed works to complete the job will be included within the price. | m² | 1
45 | Cement plastering with crack repairing: Supply of materials, tools and manpower to repair wall cracks and remove the damaged cement plastering of walls & fence by removing the damaged cement plastering minimum 35cm at each side of the crack, then treat the cracks with crack filler approved by manufacture with cement mortar 1:3 and using SBR at a rate of 50gr per m2, later putting a layer of metal chicken mesh 10 cm overlap each side on the area with 3 layers of cement plastering 1:3. All needed works to complete the job, will be included within the price. | m² | 1
46 | Cement Plastering without crack repairing: Supply of materials, tools and manpower to remove the damaged cement plastering from the exterior or internal walls and fences and apply new layer of cement plastering (20 mm thickness) using cement and sand mortar (1:3) and using aluminum straight edges.Also include removing all the rubble to a site approved by local authorities. All needed work to complete the job will be included within the price. | m² | 1
47 | Rendering: Supply of materials, tools and manpower for applying rendering (5 mm thickness)using white cement rendering with cement-stone powder (1:5). the work include add colors to Rendering accordance to the instructions of the supervising Engineer.Including horizontal and vertical leveling and water curing. Also include removing all the rubble to a site approved by local authorities . All needed work to complete the job will be included within the price. | m² | 1
48 | Lime Plastering (New works) Provision of materials, labour and equipment and all other necessary activities that are required for plastering on new stone or brick construction. Lime plastering mix proportions will be as follow; 1.75 (مسحوق الجير المطفأ)lime: 0.25 ( حبيبات الحجر)limestone grains: 2 sand. The contractor will complete the job as per the instructions of supervising engineer. | m² | 1
49 | Lime Plastering (Repair) : Provision of materials, labour and equipment and all other necessary activities that are required for plastering on stone or brick construction. the Lime plastering mix proportions will be as follow; 1.75 (مسحوق الجير المطفأ)lime : 0.25 ( حبيبات الحجر)limestone grains : 2 sand. Ensure the equipment is dry and clean before use. The work also includes removing the old layer of plastering. The contractor will complete the job as per the instructions of supervising engineer. | m² | 1
Lime stone (Hillan) work
50 | Polishing of Lime stone (Hillan) & Marble : Supply of materials, tools and manpower for polishing the lime stone (hillan) & Marble, including filling all the cracks, joints and holes of the lime stone & Marble with white cement paste and apply a layer of varnish . All needed works to complete the job will be included within the price. | m² | 1
51 | Masonry works (limestone-Hillan): Supply of materials, tools and manpower for packaging the walls with limestone thickness 5cm (natural stone), approved type by the engineer and it should come without the rust(stone pulp), the cost includes using BRC, metal wire, fixing pins, cement mortar, sand, staple materials, seam with white cement mortar (Ghubrah) (1: 1), filling joints and all required work and according to technical specifications, drawings and guidance of the supervising engineer. The cost of the work shall include all the requirements to complete the job.SEE ATTACHED DRAWING #6. | m² | 1
52 | Masonry works (Koben limestone): Supply materials, tools, and the manpower to the work of wrapping the upper face of the fence with a smooth Kubin limestone thickness (5) cm and a width (W) cm rounded from both sides of a good type of clean and free of rust stains (stone pulp), including the price mortar cement and sand and stabilizers for stone (staph) and sutures with cement white and (Ghubrah) (1:1) and fill the joints and all required work and technical specifications and remove the damaged parts with the mortar and as directed by the supervising engineer.
a | width 35 cm | m.l | 1
b | width 25 cm | m.l | 1
53 | Limestone Window Frame: Supply of materials, tools and manpower to remove the damaged limestone window frame and removing of all the debris to a site approved by local authority, then install new limestone window frame using cement sand mortar. Dimensions width 30cm thicknees 5cm rounded from one side. The work includes using BRC 200x200x5mm under the limestone. the cost includes using BRC, metal wire, fixing pins, cement mortar, sand, staple materials. All needed work to complete the job will be included within the price.SEE ATTACHED DRAWING #6. | m.l | 1
54 | Crown of column from limestone (Hillan): Supplying materials and tools and doing packaging work from the top side of the columns with a cup in the form of a crown using the smooth limestone thickness (10) cm with dimensions (70 × 80) cm from the bottom, then working in it in the form of crumbs so that its dimensions from the top (80 × 90) cm and Of good quality, clean and free from rust stains (stone pulp), including price, cement mortar, sand, stone-fixing material (staph), seams with white cement mortar and (Ghubrah) (1:1), filling joints and everything required by work and technical specifications and directed by the supervising engineer. | no. | 1
Alabaster works
55 | Alabaster Wall Covering without Carving Provision of materials, labour and equipment and all requirements to cover walls with the alabaster without carving with a width of 10 cm, 20 cm, 25 cm, and 30 cm and a thickness of not less than 5 cm, according to its lengths. The price includes the use of a BRC mesh layer of 15 * 15 cm and 6 mm D with cement mortar and sand 1: 3. All finishing to be dry sanded, followed by wet sanding for scratch free, polished appearance and further sealed with a natural locally available porous stone sealer. All works in accordance to the instructions of the supervising Engineer. | m² | 1
56 | Alabaster Window-door Frame : Supply of materials, tools and manpower to remove the damaged limestone window frame and removing of all the debris to a site approved by local authority, then install new Alabaster window using cement sand mortar. Dimensions width 30cm thicknees2cm rounded from two side. the cost includes using BRC, metal wire, fixing pins, cement mortar, sand, staple materials. The work includes using BRC under theAlabaster. All needed work to complete the job will be included within the price. | m.l | 1
57 | Alabaster Wall Covering with Carving Provision of materials, labour and equipment and all requirements to cover walls with the alabaster including carving with a widthof 10 cm, 20 cm, 25 cm, and 30 cm and a thickness of not less than 5 cm, according to its lengths. The price includes the use of a BRC mesh layer of 15 * 15 cm and 6 mm D with cement mortar and sand 1: 3 . All finishing to be dry sanded, followed by wet sanding for scratch free, polished appearance and further sealed with a natural locally available porous stone sealer. All works in accordance to the instructions of the supervising Engineer. Drawing Attached | m² | 1
58 | Alabaster Frames / Architraves without Carving Provision of materials, labour and equipment and all requirements for frames/architraves (Coping) constructed from alabaster without carving at a width of 20 cm, and 30 cm and the thickness is as existed, according to its lengths. The price includes the use of a BRC mesh layer of 15 * 15 cm and 6 mm D with cement mortar and sand 1: 3. All finishing to be dry sanded, followed by wet sanding for scratch free, polished appearance and further sealed with a natural locally available porous stone sealer. All works in accordance to the instructions of the supervising Engineer. | m³ | 1
59 | Alabaster Arches without Carving Provision of materials, labour and equipment and all requirements to build arches, without carving, with a width of 20 cm and 30 cm and the thickness is as existed, according to its lengths. Cement and sand mortar 1:3 is used with rolled bolts to the walls. price will include the cutting, carving and installation of alabaster elements that reflects the previous destroyed elements. All finishing to be dry sanded, followed by wet sanding for scratch free, polished appearance and further sealed with a natural locally available porous stone sealer. All works in accordance to the instructions of the supervising Engineer. | m³ | 1
60 | Alabaster Frames / Architraves with Carving Provision of materials, labour and equipment and all requirements for decorative frames/architraves (coping) with carving, width of 20 cm and 30 cm and the thickness is as existed, according to its lengths. Cement and sand mortar is used with rolled bolts to the walls. All finishing to be dry sanded, followed by wet sanding for scratch free, polished appearance and further sealed with a natural locally available porous stone sealer. All works in accordance to the instructions of the supervising Engineer. | m³ | 1
61 | Alabaster Arches with Carving Provision of materials, labour and equipment and all requirements for build arches, with carving, width of 20 cm and 30 cm and the thickness is as existed, according to its lengths. Cement and sand mortar is used with rolled bolts to the walls. All finishing to be dry sanded, followed by wet sanding for scratch free, polished appearance and further sealed with a natural locally available porous stone sealer. All works in accordance to the instructions of the supervising Engineer. | m³ | 1
62 | Alabaster Circular Columns without Carving Provision of materials, labour and equipment and all requirements for building circular columns according to the required measurements and without carving with the use of rolled bolts and fastening it with reinforcing steel between the parts of the column. All finishing to be dry sanded, followed by wet sanding for scratch free, polished appearance and further sealed with a natural locally available porous stone sealer. All works in accordance to the instructions of the supervising Engineer. | m³ | 1
63 | Alabaster Circular Columns with Carving Provision of materials, labour and equipment and all requirements for building circular columns according to the required measurements and with carving with the use of rolled bolts and fastening it with reinforcing steel between the parts of the column and according to the technical specifications and instructions of the supervising engineer. All finishing to be dry sanded, followed by wet sanding for scratch free, polished appearance and further sealed with a natural locally available porous stone sealer. All works in accordance to the instructions of the supervising Engineer. | m³ | 1
64 | Alabaster Square Columns without Carving Provision of materials, labour and equipment and all requirements for building square columns according to the required measurements and without carving with the use of rolled bolts and fastening it with reinforcing steel between the parts of the column. All finishing to be dry sanded, followed by wet sanding for scratch free, polished appearance and further sealed with a natural locally available porous stone sealer. All works in accordance to the instructions of the supervising Engineer. | m³ | 1
65 | Alabaster Square Columns with Carving Provision of materials, labour and equipment and all requirements for building Square columns according to the required measurements and with carving with the use of rolled bolts and fastening it with reinforcing steel between the parts of the column. All finishing to be dry sanded, followed by wet sanding for scratch free, polished appearance and further sealed with a natural locally available porous stone sealer. All works in accordance to the instructions of the supervising Engineer. | m³ | 1
66 | Alabaster Miscellaneous Parts with Carving Provision of materials, labour and equipment and all requirements for building alabaster miscellaneous parts in different dimensions with carving. All finishing to be dry sanded, followed by wet sanding for scratch free, polished appearance and further sealed with a natural locally available porous stone sealer. All works in accordance to the instructions of the supervising Engineer. | m³ | 1
67 | Alabaster Repair with Carving Provision of materials, labour and equipment and all requirements to repair the damaged parts of the Alabaster with carvings. (e.g. fractures, cracks, holes, detachment, partial loss, blistering cleaning, degradation, loss of polishing etc) The price includes filling voids and substitute the missing and damaged parts using materials with the same colors and with good adhesion properties. All finishing to be dry sanded, followed by wet sanding for scratch free, polished appearance and further sealed with a natural locally available porous stone sealer. All works in accordance to the instructions of the supervising Engineer. | m² | 1
68 | Alabaster Repair without Carving Provision of materials, labour and equipment and all requirements to repair the damaged parts of the Alabaster without carving. (e.g. fractures, cracks, holes, detachment, partial loss, blistering cleaning, degradation, loss of polishing etc) The price includes filling voids and substitute the missing and damaged parts using materials with the same colors and with good adhesion properties. All finishing to be dry sanded, followed by wet sanding for scratch free, polished appearance and further sealed with a natural locally available porous stone sealer. All works in accordance to the instructions of the supervising Engineer. | m² | 1
69 | Polishing alabaster (old parts) Provision of materials, labour and equipment and all requirements to Polishing alabaster for all the required for old parts (walls, frames, arches, columns, etc.)the price includes filling the joints with the same color of the alabaster and according to the technical specifications and to the instructions of the supervising Engineer. | m² | 1
Painting
70 | Emulsion painting (internal): Supply of materials, tools, and manpower to paint the interior walls and ceilings, with 3 layers of emulsion paint. The job includes cleaning the walls and ceilings, removing the dirt and dust, repairing all the cracks and filling all the holes before painting. All needed works to complete the job should be included within the price. | m² | 1
71 | Plastic painting (extrenal): Supply of materials, tools and manpower to paint the exterior walls and fence, with three layers of plastic (silicon water proof) paint. The job includes cleaning the walls, removing the dirt and dust, repairing all the cracks and filling all the holes before painting. All needed works to complete the job should be included within the cost. | m² | 1
72 | High Qaulity External Paint UV Resistant and Water Resistant Supply of materials, tools and manpower to paint the exterior walls, with three layers of plastic (UV resistant and Water Resistant, 100% acrylic) paint. The job includes cleaning the walls, removing the dirt and dust, repairing all the cracks and filling all the holes before painting. All needed works to complete the job should be included within the cost. | m² | 1
73 | Oil Painting (for metals): Supply of materials, tools and manpower to paint the steel doors, windows, and internal walls with a paint (1.50m height) for skirting using 3 layers of oil paint. The job includes cleaning, removing the dirt and dust, repairing all the cracks and filling all the holes before painting. All needed works to complete the job should be included within the cost. | m² | 1
74 | Mineral Based Natural Lime Wash: Provision of materials, labour, equipment and all other necessary activities that are required for painting walls and any other places defined by the supervising engineer with natural limewash. Hydrated lime putty ( 1 lime: 2 water) is thinned and tinted with natural pigments. 4 coats application and 24 hours curing for each layer. The work includes applying a prime coat of lime with proportion (1 Lime: 20 water). The price includes the addition of acrylic binder (100 gm for 1 KG mixed hydrated Lime), any preparatory works required prior to the painting, such as filling and repairing all holes and cracks, removal of nails and flaking old paint, scraping away any loose plaster, etc. The painting work should be done by brush tool. All works should be done according to instructions of the supervision engineer. Colour samples will be provided. | m² | 1
75 | Waterproof Painting: Supply of materials, tools and manpower to paint the exterior and interior walls with three layers of (water proof) paint. The job includes cleaning the walls, removing the dirt and dust, repairing all the cracks and filling all the holes before painting. All needed works to complete the job, shall be included within the price. | m² | 1
Suspended Ceiling
76 | Suspended Ceiling : Supply of materials, tools and manpower to install suspended ceiling 60x60 cm, 10mm thickness, by using necessary accessories L, T sections, hold down clips, galvanized steel rod 5mm (1.2x1.2m) for fixing with the ceiling by screws. The price includes the removal of old damaged suspended ceiling if there, dumping of all debris to a site approved by local authorities, in case it is needed. All needed work to complete the job will be included within the price.
a | Gypsum board | m² | 1
b | Plastic | m² | 1
77 | Acoustic suspended ceiling: Supply of materials, tools and manpower to install suspended ceiling 60x60 cm (acoustic boards), 12 mm thickness, by using all necessary accessories L, T sections, galvanized steel wire 2mm for fixing on the ceiling by screws, sample should submitted to supervisor engineer before purchasing. The price includes the removal of old damaged suspended ceiling, dumping of all debris to a site approved by local authorities, in case it is needed, as well as all needed works to complete the job. | m² | 1
78 | Gypsum Board Ceiling Supply of materials, tools and manpower to install Gypsum Board Ceiling using sheets of gypsum (1.2mX2.4mX1cm).Procedure of laying framework for gypsum board ceiling • The first member laid for the ceiling is perimeter channel to determine the depth of the false ceiling. • Soffit cleat is screwed in through fasteners in to concrete ceiling. At the other end of soffit cleat hanger is joined with the help of screws. •These hangers are joined to U shaped main T through screws. The minimum distance between two main T is 1.20m. • Main T is laid vertically. Then main T is either clipped to cross T or screwed to cross T. • Cross T is laid in opposite direction of main T making grid pattern. The minimum distance between two cross Tis 50cm. •Cross T is basically U in Osection corners folded outwards. •Then gypsum board is screwed to channels or cross T with the help of star screw made up of iron. The Gypsum board size used is (1.2mX2.4mX1cm) with 25 screws. • To give finish to the join of two square edge gypsum board firstly we make gap of 6mm between them. then they are filled with pop and reinforced with 50mm wide fibre tape. Pop finished plaster is then spread over the join of two boards, leveled and trovelled to a smooth finish to a thickness of 2-5mm.. The price includes the removal of old damaged suspended ceiling, dumping of all debris to a site approved by local authorities, in case it is needed, as well as all needed works to complete the job. See attached drawings | m² | 1
Floor Finishing
79 | New Mosaic Tiles for floors: Supply of materials, tools and manpower to apply mosaic tiles for floors, using cement sand mortar(1:3), filling the joints with white cement. All needed work to complete the job will be included within the price.
a | size 30*30 cm | m² | 1
b | size 40*40 cm | m² | 1
80 | Repair Mosaic Tiles for floors: Supply of materials, tools and manpower to remove damaged tiles and place Mosaic tiles then apply mosaic tiles for floors, using cement sand mortar(1:3), filling the joints with white cement. All needed work to complete the job will be included within the price.dumping of all debris to a site approved by local authorities, in case it is needed, as well as all needed works to complete the job.
a | size 30*30 cm | m² | 1
b | size 40*40 cm | m² | 1
81 | In-situ Polishing and glazing of floor terrazzo(mosaic) tiles: Supply of materials, tools and manpower for polishing and glazing of the terrazzo(mosaic) tiles. The price includes filling the joints with white cement paste. All needed work to complete the job will be included within the price. | m² | 1
82 | Granite tiles for floors: Supply of materials, tools and manpower to remove damaged tiles and place granite tiles (60x60cm) using cement sand mortar(1:3), filling the joints with white cement paste . All needed work to complete the job will be included within the price. | m² | 1
83 | Basalt Tiles for Floors of Entrance and tread & riser of steps stair Supply of materials, tools and manpower to to remove the damaged Mosaic tiles and dumping it to a place approved by local authority, then apply Basalt tiles thickness 2.5cm Grey color for floors and face & riser of steps stair It must be polished and free from cracks and holes.(dimensions according to the Measurements of the tread and riser in the stair) , using cement sand mortar(1:3), filling the joints wilh clear fine sand.Work includes preparation the tread and riser in case need to reduction thickness of old concrete floor or build before covering the stair In order to make the riser height about ranges(18-20). All needed work to complete the job will be included within the price. | m² | 1
84 | Porcelain Tiles for Floors: Supply of materials, tools and manpower to apply nun-slip porcelain tiles for floors size 40*40cm or dimension according to the approved samples) , using cement sand mortar(1:3), filling the joints with white cement paste. All needed work to complete the job will be included within the price. | m² | 1
85 | Non Slip Ceramic tiles 30x30cm for floors: Supply of materials, tools and manpower to apply non slip ceramic tiles 30x30cm for the toilatte floors using cement mortar (1: 2) and/ or replace the damaged parts with new tiles from the same type. The price includes filling the joints with white cement paste. All needed work to complete the job will be included within the price. | m² | 1
86 | Mosaic Tiles for Floors and face & riser of steps stair: Supply of materials, tools and manpower to to remove the damaged mosaic tiles and dumping it to a place approved by local authority, then apply Mosaic tiles for floors and face & riser of steps stair (dimension according to the approved samples) , using cement sand mortar(1:3), filling the joints with white cement paste. All needed work to complete the job will be included within the price. | m² | 1
87 | Granite steps/treads for stair: Supplying materials, tools and manpower to remove damaged steps/treads and apply granite steps, 3 cm thickness for the tread, and 2cm for the riser, 30cm width and 1.2 m length by using cement mortar (1:3) and rounding the external edges, filling joints by white cement mortar. All the requirement to do job. | m² | 1
88 | Mosaic steps(Tread and Riser) for stair: Supplying materials, tools and manpower to remove damaged mosaic steps and dumping it to a place approved by local authority, then apply new mosaic steps,5 cm thick for the tread and 3cm for the riser and with 30cm width and 1.4m length using cement mortar (1:3) and rounding the external edges, filling joints by white cement mortar. All needed work to complete the job will be included within the price. | m² | 1
89 | Rubber Floor Tile: Supplying materials, tools and any necessary equipment and covering for the concrete floor under children playground slides with rubber tiles heat resistant from 40 - 100 °C, UV resistance and water-resistant thickness not less than 2cm and dimensions of 40cm* 40cm. All needed works to complete the job will be included within the price. | m² | 1
90 | Floor Coating with Epoxy: Supply of materials , tools and manpower for coating the interior concrete floor with epoxy. The price included cleaning and polishing the floor, level the floor with self-leveling material (Sika level) with a thickness of 1-3 cm to obtain level floor, coating with (primer Sika Floor 161) then coating the floor with a self-leveling epoxy (Sika Floor 263 SL) with a thickness at least 2 mm resistant to compression , friction, oily , antibacterial and chemical materials, and the color and shape shall be chosen by the site engineer. All needed works to complete the job will be included within the price. | m² | 1
Finishing of Roads & Walkway
91 | Finishing floor of Roads by Biharton tiles: Supply and provide all materials, tools and machines to install Biharton tiles(20x10x5cm); the work includes the details below:1-Remove finishing materials plain cocrete to depth 20cm in order the floor level of bharton floor to be equal in level to rest of the concrete floor.2- casting (10cm ) plain concrete (C25MPa) using sulphate resistance cement with BRC layer (200x200x5mm).3-apply Biharton tiles grey color of best quality for floors, using cement sand mortar(1:3), filling the joints with white cement coloring to grey color.4- Price includes the removal of all existing concrete above the base level, in addition to any uprises such as manholes or main sewers etc. Samples of manhole covers of septic tanks. to be submitted and approved by Ta'afi engineer prior to starting.All needed work to complete the job will be included within the price. | m² | 1
92 | Gutter Repair and Steel Gutter Installation: Provision of materials, labour and equipment, and all requirements to repair the old damaged central gutter along with the path of the road using cement mortar (1: 3 Sand with SBR). Price includes substituting damaged parts and casts concrete base (25Mpa) for the gutter 10*10 cm and 6 m length. the joint should be filled with Sika construction sausage or equivalent. And install the steel gutter cover (40 cm in width) the steel gutter connected with the frame and fixed hinges at 1 m (the steel gutter is movable for cleaning) .All needed work to complete the job will be included within the price. | m.L | 1
93 | Walkway Tiles(shiteker): Supply of materials, tools and machineries to apply (shiteker tiles) of the internal roads and installing using cement sand mortar (1:3),backfilling. All the needed work to complete the job shall be included within the price. | m² | 1
94 | Walkways with stones: Supply and provide all materials, tools and machines to cast the walkways with natural stones (stones with different surface area 25 to 500cm2), the work include compacting of the ground under the path, applying layer of plain concrete (1:2:4) or crashed aggregate, and using crashed sand, and concrete (1:3) in-between the stones, the surfaces should be level, and the path sides should be locked by reinforced concrete (15x30 cm), and all required work (painting of the sides or joints), considering required elevations and necessary slope according to supervising engineer. | m² | 1
95 | Walkways Interlock tiles: Supply and provide all materials, tools and machines to install interlock tiles; through compacting of ground by applying sub-base when necessary and with required thickness according to supervisor engineer (5-20 cm), and providing crashed sand under the tiles with thickness not less than (10cm)), then applying layer of interlock tiles (5cm), with cement-sand mortar (1:3), with locking the path from both side with reinforced concrete (BRC-6mm) (10x30cm, ratio 1:3), and all required work, considering required elevations and necessary slope according to supervising engineer. | m² | 1
96 | Colors Interlock- garden edging : Supply materials, tools and labor to supply new Interlock dimensions (30x10x10 cm) ,the work include good fixing for Interlock in soil of garden, according the agricultural specifications. All the needed works to complete the job shall be included within the price. | m.l | 1
Weeden Works
97 | Wooden Stage Supply and install wooden stage of (L*W*0.3 m) made of Wood(Sizes are 4"x1") . It must be supported by (3"x3") wood size at every 40 cm dustrubuted along the short length and with studs at 40 cm in both directions, the type of the wood is Jam "خشب جام", with paint by Shellac (Known locally as "Damaluk دملوك". Paint must be applied in multiple layers along with using smooth sandpaper (Grit 1000 or more). Finish layer of wax must be applied to provide smooth touch for the surface. Finish surface must be silky and free from drip marks. All contacted wood pieces must be fixed using wood adhesive, wood joints (such as half lap, Tongue and Groove, Box Joint, Biscuit Joint, Butt Joint etc.) and Nail or Screws. | m² | 1
98 | Old Wood Repair and Paint (UV and Water Resistant) The work includes supplying material, tools and manpower to removing old paint from wood using grinder and sandpaper of different grit (up to 700 or more). The work include repairing the cracks and defects with proper materials. Paint with specialized paint UV resistent and Water proof with the right color and must not hide wood texture. Paint must be applied in 3 layes or more along using smooth sandpaper. Finish surface must be silky free from drip marks. External layer might be replaced if it is heavely detriorated with same wood type and thickness or if grinding the old paint will detriorate it and any other accessories. All work must be done according to the supervising engineer's instructions. | m² | 1
Walls Covering
99 | Ceramic tiles for walls
a | Supply of materials, tools and manpower to apply ceramic tiles using cement mortar (1:2) and straight edge. the price includes filling the joints with white cement plaster. The price includes one layer of cement splash dash under ceramic tiles with cement-sand mortar. All needed work to complete the job well be included within the price. | m² | 1
b | Supply of materials, tools, and manpower to install high quality ceramic tiles. The price includes all the material needed to install the ceramic tiles using polymer enhanced cementitious mortar and all other material necessary to have the work complete. also, the work includes cement plaster the wall before applying the ceramic tiles. All work should be done according to the instructions of the supervising engineer. | m² | 1
100 | Alabaster tiles for walls Supply of materials, tools and manpower to apply Alabaster tiles thickness 2cm using cement mortar (1:2) and straight edge. the price includes filling the joints with white cement past. The price includes one layer of cement splash dash under Alabaster tiles with cement-sand mortar. All needed work to complete the job well be included within the price. | m² | 1
101 | Walls Cladding with MDF: Supply of materials, tools and manpower to remove all damaged wood cladding and install new MDF wall caldding by using longitudinal strips of 30 cm width including removing the existing wood cladding and dumping of all debris to specific site approved by local authorities. PVC strips installation should use U,L section and all necessary accessoris. Contractor should submit samples for approval. All needed works to complete the job, will be included within the price. | m² | 1
102 | Skirting: Supply of materials, tools and manpower to apply ceramic skirting 10cm height using cement mortar. The price includes removing of all the damaged skirting and dumping it to a site approved by local authority, filling the joints with white cement paste. All needed work to complete the job will be included within the price. | m.l | 1
Roads Work
103 | Road Paving (stabilizer): supplying the materials, tools, and manpower to pave concrete paving with concrete asphalt with the thickness of (10cm) stabilizer, after the compact with a percentage of not less than (97%), The work includes spraying prim coat with a rate of 1 liter per square meter, according to the conditions and technical specifications of roads and bridges (R9), and as directed by the supervising engineer and the price includes design the equation modern blending, and perform all necessary laboratory tests. | m² | 1
104 | Road Paving (Binder): supplying the materials, tools, and manpower to pave concrete paving with concrete asphalt with the thickness of (7cm) Binder, after the compact with a percentage of not less than (97%), The work includes spraying tack coat with a rate of 0.5 liter per square meter, according to the conditions and technical specifications of roads and bridges (R9), and as directed by the supervising engineer and the price includes design the equation modern blending, and perform all necessary laboratory tests. | m² | 1
105 | Curbstone: Supply of materials, tools and machineries to apply a new curbstone of the internal roads and installing using cement sand mortar (1:3),backfilling with clean clay for back of curbstone with width not less than 1 m and ainting the curbstone by certified paints for road works. All the needed work to complete the job shall be included within the price. | ml | 1
106 | Replacing Damaged parts of Curbstone: Supply of materials, tools and manpower to remove all the damaged parts of the curbstone to a site approved by local authorities, then provide concrete base (200*850) mm beneath the curbstone, laying concrete curbstone (750*300) mm, modulus of rupture (3.5MPa), providing concrete gutter(100mm from the outer face and 70mm from the curbstone face) with required slope after laying the curbstone, filling the back of the curbstone with the concrete minimum (200x150mm), filling all joints of the curbstone using cement sand mortar (1:3 ) and conducting all the required laboratory tests. All the needed works to complete the job shall be included within the price. All works should be according to the technical specifications for roads. SEE ATTACHED DRAWING #4. | m.l | 1
107 | Street painting works: Supplying equipment, tools, machines, manpower and preparing thermal paint (thermoplastic) for the roads in yellow and white from good origin and according to the technical and international specifications of the roads, and conducting planning for both sides of the street in a linear direction and continuously in yellow color, and conducting an intermediate planning along the street and intermittently, dye 6 meters and leave 6 Another meter in white color, By using a street planner, with spray a light reflective glass. The price includes street cleaning and all that it takes to work as directed by the supervising engineer. | m.l | 1
108 | Curbstone Painting : Supply of materials, tools and manpower to paint the curbstone using (white and orange) plastic paint and should be resistant to weather and friction. The price includes removing the old painting from the curbstone and dump it to a site approved by local authority. All the needed works to complete the job shall be included within the price. All works should be according to the technical specifications for roads. | m.l | 1
109 | Reinforced Concrete works for Internal Streets: Supply of materials, tools and manpower for: 1-Demolishing and removing the damaged old concrete to a site approved by local authorities. 2-Compaction of the base up to (90%) of MDD. 3-Casting reinforced concrete rigid pavement using (C25MPa), 20cm thick with BRC (150x150x6mm) using sulphate resistance cement. 4-Providing precast middle draining of (50x10cm) at the center of the street. 5-The price includes providing concrete covers, proper slope, machinery trawling, making joints every 5.0m (both directions) and filling it with cement sand mortar (1:3). 6-The price also includes conducting all the required laboratory tests. All the needed works to complete the job shall be included within the price. All works should be according to the technical specifications for roads. SEE ATTACHED DRAWING #40. | m² | 1
Water treatment for roof and walls
110 | The roof treatment: Supply of materials, tools, and manpower and all related and required work to prevent moisture in the roofs. by using special materials in the capillary crack in the roof by: 1-Removing the existing cement tiles with attached materials; sand, clay, and bitumen materials. 2-Clean the roof with water by water jet pressure machine, and steel brushes if required. 3- Apply a layer of waterproofing (Isocam) with thickness not less than 4mm, and guarantee of not less than 10 years, with testing of 72 hours, and from the good origin approved by the site engineer, the layer should cover the roof properly and high of wall parapet not less than 40cm. all materials and work should be approved by technical engineers. | m² | 1
111 | Changing the Sealant(Mastic) of Expansion Joints: Supply of materials, tools and manpower to remove the exsiting sealant (mastic) of the expansion joints, The work includes cleaning the joinits by air compressor to make sure the joints are cleaning and apply new sealant(mastic)in joints. All needed work to complete the job will be included within the price." | m.l | 1
112 | Interior Expansion joint Covers: Supply of materials, tools and manpower to inject the interior expansion joints (walls and ceiling) with foam and fill the expansion joints of the floors with mastic sealant, then install aluminum cover 20cm width, with rubber between the two pieces of plates and using screws to fix. All needed works to complete the job will be included within the price." | m.l | 1
113 | Roof Waterproofing Work: Supply of materials, tools and manpower for roof work. By cleaning concrete surface and follow up steps as below: 1- Apply one layer of bitumen flint coat. 2- Apply two layers of bituminous felt-Izo gam (4 mm thickness) laid in the opposite direction( the overlaps of the bituminous felt should be not less than 15 cm and sealed with bitumen). 3- Apply one layer of bitumen flint coat. 4- Laying of compressed high density Styrofoam 5cm for all roof area. 5- Place mosaic tiles of dimensions 30x30cm, type #2, thickness 3 cm, apply expantion joints 2 cm width every 3.6 m for both directions, using cement mortar (1:3), cement and sand mortar bed, cutting, fittings, trims, curve edges, pointing with stock. 6- Filling all expansion joints by Approved Mastic, grouting tiles joints by white cement, polished & glazed mechanically on site. 7- Rain water slope should be given and designed as per standards. All needed works to complete the job will be included within the price. SEE ATTACHED DRAWING #55. | m² | 1
114 | Roof Waterproofing ( for surface leaks ): Supply of materials, tools and manpower for roof repairing work. including clean,wash and removing the rubble from the surfaces and follow up steps as below: 1- Treatment of cracks and wall connection area with roof, by using polyurethane foam 2- Apply one layer of polyurethane primer coat 3- Painting the surface by using 3 layers of polyurethane (rubber membrane paint) of 2 mm thickness All needed works to complete the job will be included within the price. | m² | 1
115 | Roof Waterproofing Work: Supply of materials, tools and manpower for roof work. By cleaning concrete surface and follow up steps as below: 1- remove all deamage parts from roof shiteker tiles,mosic tiles,solid cement mortor,sand and remove all the debris to a site approved by local authorities. 2- Clean the roof with water by water jet pressure machine, and steel brushes if required. 3-Apply the flexible sealent for joints ( Sausage ). 4- Apply one layer of bitumen flint coat. 5- Place mosaic tiles of dimensions 30x30cm, type #2, thickness 3 cm, apply expantion joints 2 cm width every 3.6 m for both directions, using cement mortar (1:3), cement and sand mortar bed, cutting, fittings, trims, curve edges, pointing with stock. 6- Filling all expansion joints by Approved Mastic, grouting tiles joints by white cement, polished & glazed mechanically on site. 7- Rain water slope should be given and designed as per standards. All needed works to complete the job will be included within the price. | m² | 1
116 | Treatment of Roof Water Ponds (Screed Concrete): Supply of materials, tools and manpower to treat the roof water ponds (screed concrete) using self levelling concrete (from zero up to 4 cm thickness). The price includes cleaning the roof, removing all the collected water and drying the surface before applying the treatment. All needed work to complete the job will be included withing the price. | m² | 1
117 | Treatment of Roof -Mosaic Tiles for roofs: Supply of materials, tools, and manpower to apply mosaic tiles size 30*30 for roofs. according to the specifications of the work below: 1-Removing the existing cement tiles with attached materials; sand, clay, and bitumen materials. 2-Clean the roof with water by water jet pressure machine, and steel brushes if required. 3- apply mosaic tiles of dimensions 30x30cm, type #2, thickness 3 cm, apply expantion joints 2 cm width every 3.6 m for both directions, using cement mortar (1:3), cement and sand mortar bed, cutting, fittings, trims, curve edges, pointing with stock. 4- Filling all expansion joints by Approved Mastic, grouting tiles joints by white cement, polished & glazed mechanically on site. 5- Rain water slope should be given and designed as per standards. All needed works to complete the job will be included within the price. | m² | 1
118 | Roof Waterproofing ( for Joints leak ): Supply of materials, tools and manpower for roof repairing work. including clean,wash and removing the rubble from the Joints for cracks between (1- 4 cm ,width), and follow up steps as below: 1- Apply the compacted sponge rode according to the joint width. 2- Apply one layer of polyurethane primer coat. 3- Apply the flexible sealent for joints ( Sausage ). All needed works to complete the job will be included within the price. | m.l | 1
The Doors
119 | PVC door with frame (WxH): Supply of materials, tools and manpower to install PVC doors with frame. The PVC section should be wide section. The lower 1.0m portion of the door to be covered by PVC sheets and the upper portion will be covered by frosted glass 6mm. The price includes hinges, handles, locks and frosted glass (6mm). All needed works to complete the job should be included within the cost.SEE ATTACHED DRAWING #48. | m² | 1
120 | PVC Doors with Frame: Supply of materials, tools and manpower to install PVC doors with frame. The PVC section should be wide section (Min. 60mm). Price of the work shall include removing the damaged doors and hinges, handles, locks and repairing the door edges from both sides . All needed works to complete the job, will be included within the price. SEE ATTACHED DRAWING #48. | m² | 1
121 | PVC Doors with out Frame: Supply of materials, tools and manpower to install PVC doors with out frame . The PVC section should be wide section (Min. 60mm). The Price of the work shall include removing the damaged doors and hinges, handles, locks. All needed works to complete the job, will be included within the price. SEE ATTACHED DRAWING #48. | m² | 1
122 | Steel door with the frame (WxH): Supply of materials, tools and manpower to install steel door with frame, with steel plate gauge 18(1.41mm) on double face, using steel tube 25x25x2mm, including a layer of Styrofoam to be placed between the two faces, hinges, doors handles, locks and fixing a stopper on the floor or wall. The price of work includes the painting of steel door using anti-rust and 2 layers of oil paint.the work include repairing the gypsum plastering and cement plastering of the edges. All needed work to complete the job will be included within the price.SEE ATTACHED DRAWING #53. | m² | 1
123 | Steel Door without Frame: Supply of materials, tools and manpower to install steel door without frame, with steel plate gauge 18(1.21mm) on double face, using steel tube 25x25x1.8mm, including a layer of Styrofoam to be placed between the two faces, hinges, doors handles, locks and fixing a stopper on the floor or wall. The Price of the work shall include removing the damaged doors and painting of steel door using anti-rust and 2 layers of oil paint. All needed work to complete the job will be included within the price. See attached drawing. SEE ATTACHED DRAWING #53. | m² | 1
124 | Steel door with the frame (WxH)-Heritage Shape: Supply of materials, tools and manpower to install steel door with frame, with steel plate gauge 18(1.41mm) on one face, using outer steel tube75x40x1.8mmfor frame, for internal members using square steel tube 20x20x1.4 mm and plate width 10mm thickness 2mm, hinges, doors handles, locks and fixing a stopper on the floor or wall. The price of work includes the painting of steel door using anti-rust and 2 layers of oil paint.the work include repairing the gypsum plastering and cement plastering of the edges. All needed work to complete the job will be included within the price.SEE ATTACHED DRAWING #46. | m² | 1
125 | Aluminum Doors with Frame (WxH): Supply of materials, tools and manpower to install aluminum doors with frame. The aluminum section should not be less than 50mm width. The lower 1.0m portion of the door to be covered by aluminum sheets and the upper portion will be covered by glass 6mm. The price includes hinges, handles, locks and frosted glass (6mm) . All needed works to complete the job, will be included within the price.SEE ATTACHED DRAWING #50. | m² | 1
126 | Wooden doors (WxH) with frame(WxH): Supply of materials, tools and manpower to install teak (saj) wooden doors with red cedar (jaw) frame. Price of the work shall include removing the damaged doors and frames, door locks, handles, hinges, teak painting and varnish painting. Also repairing the gypsum plastering and cement plastering of the edges .All needed work to complete the job will be included within the price.SEE ATTACHED DRAWING #10. | m² | 1
127 | Wooden doors without Frame(WxH): Supply of materials, tools and manpower to install teak wooden ( saj ) doors with red cedar ( jaw) wooden without frame.The Price of the work shall include removing the damaged doors and frames, door locks, handles, hinges, teak painting and varnish painting. Also repairing the gypsum plastering and cement plastering of the edges and repaint the old frame as same as the new door .All needed work to complete the job will be included within the price. See attached drawing.SEE ATTACHED DRAWING #10. | m² | 1
128 | Steel burglary door protection (WxH): Supply of materials, tools and manpower for fabricating and installing steel burglar protection, fabricated from steel outer frame L (75x75x3mm), with square steel tube (50x50x3mm) and sub divider (12x12x2mm) every 15 cm. The work includes the painting using two-layers anti-corrosion and three-layers of oil paint, as well as all needed works to complete the job. | m² | 1
129 | Sliding steel door (WXHm)one leaf: Supply of materials, tools and manpower to remove the damaged sliding steel door and removing the debris and rubble to a site approved by local authority, then install new slide steel door (one leaf), including plate gauge 18 on double faces, the gate has a frame of square steel pipe (100x50x2mm) and sub divider of pipe (50x50x2mm) @ 50cm c/c, slide steel frame U channel (84mm) top and bottom. Price of the work shall include installing a steel door (W1XH2.1)m a frame of angle steel (75x75x3mm) within the sliding gate. The price of work shall include painting with anti-rust and 2 layers oil paint, rollers, door handles and locks. All needed works to complete the job, will be included within the price. See attached drawing#5. | m² | 1
130 | Main Gate (WxH): Supply materials, tools and manpower to remove the damaged main gate door and install new main gate steel door of dimensions (WxH), consisting on 2 leaves. By using plate gauge 18 and steel pipe 40x40x3mm. Including door handles, hinges, locks, stopper, cleaning the steel surface from rust and dust before painting by using two (2) layers of anti-rust paint and three (3) layers of oil paint. All needed works to complete the job will be included within the price. SEE ATTACHED DRAWING #11. | m² | 1
131 | Folding Steel main gate door with the frame (WxH)m-type of the closing by fold: Supply materials, tools and manpower to remove the damaged main gate door and install new main gate steel door of dimensions (WxH)m, the door is divided into folds, each of wich is 40 cm width. consisting on 2 leaves. By using plate gauge 18 and steel pipe 40x40x3mm for internal vertical sections@40cm .using steel L section (60x60x4)mm for fram. Including door handles, hinges, locks, stopper, cleaning the steel surface from rust and dust before painting by using two (2) layers of anti-rust paint and three (3) layers of oil paint. All needed works to complete the job will be included within the price. | m² | 1
132 | Repair steel doors (Different sizes): Supply of materials, tools, machineries and manpower to repair the damaged steel doors. Price of works shall include door lock, handles, hinges, oil painting and accessories. All needed work to complete the job will be included within the price. | no. | 1
133 | Repair Wooden Doors and Frames: Supply materials, tools, and manpower to maintenance of wooden door with the frames, including work remove the damge layers of Saj, with looks, and hang, and adding new layers, with skimming the old paint, smoothing, and painting with wood paint three layers and all that is needed. | no. | 1
134 | Repair Main steel Gate: Supply of materials, tools, machineries and manpower to repair the damaged main steel door. Price of works shall include door lock, handles, hinges, oil painting, accessories, and repairing the door edges from both sides. All needed work to complete the job will be included within the price. | no. | 1
135 | Repair aluminum doors: Supply of materials, tools, machineries and manpower to repair the damaged aluminum doors. Price of works shall include door lock, handles, hinges , accessories, repairing the door edges from both sides. All needed work to complete the job will be included within the price. | no. | 1
136 | Repair PVC doors: Supply of materials, tools, machineries and manpower to repair the damaged PVC doors. Price of works shall include door lock, handles, hinges, accessories and repairing the door edges from both sides. All needed work to complete the job will be included within the price. | no. | 1
137 | Roll up Shops Door:
a | Supply of materials, tools and manpower to install a new roll up shops door with frame, with steel plate 0.5 mm, and frame thicknesse 3 mm including hinges, locks and fixing a stopper on the floor or wall approximate dimensiond 3*3 m. The Price of the work shall include removing the damaged door and painting of steel frame using anti-rust and 2 layers of oil paint and repairing the door edges (cement and gypsum plastering) from both sides. All needed work to complete the job will be included within the price." | no. | 1
b | Supply of materials, tools and manpower to Repair roll up shops door with frame. The Price of the work shall include repair the damaged door and painting of steel frame using anti-rust and 2 layers of oil paint and repairing the door edges (cement and gypsum plastering) from both sides. All needed work to complete the job will be included within the price. | no. | 1
138 | Metal Doors for Generator Shed: Supply of materials, tools and manpower to install steel doors (H×W m) by using BRC (50x50x4mm) and steel angle 75x75x3mm, 50x50x3mm and 38x38x2.5mm. The price of works includes door lock, handle, painting of steel door by using 2 layers anti-rust and 3 layers of oil painting. All needed works to complete the job will be included within the price. | m² | 1
139 | Automatic Sliding Door (L*W m) Providing, installation, Testing & Commissioning of Bi-Parting Automatic Sliding Door Operator complete with a pair of bi-parting doors and two fixed side screens. The door is activated by radar/sensors units mounted either side of the threshold. Side screen safety is provided by presence sensors mounted above the door run back area. All operating and safety accessories shall be supplied. The screen and doors shall be manufactured from proprietary Aluminum sections, single glazed with 12mm laminated safety glass. The overall screen size shall be as per site measurements. Measurements must be verified on site and shall be the vendors responsibility. The price also include the steel frame if needed for the door to be installed on it. Suitable track is included in the bottom rail of the door, to be downward pointing to prevent failure due to rubbish or dirt accumulation. All work must be done according to the supervising engineer's instructions. Warranty is one year minimum. | m² | 1
The Windwos
140 | Steel windows: Supply of materials, tools and manpower to install steel windows (using T, L and Z shapes). The price of works includes anti rust panting and two layers of oil painting, anti-insects wire mesh, handles, windows stopper ,crystal clear class 4mm thickness with paste, and repairing the window edges from both sides. All needed work to complete the job will be included within the price. | m² | 1
141 | PVC Windows: Supply of materials, tools and manpower to install PVC windows. The PVC section should be wide section. The windows include clear glass 4mm. The price includes hinges, handles, locks and frosted glass (6mm). All needed works to complete the job should be included within the cost.SEE ATTACHED DRAWING #8. | m² | 1
142 | Aluminum windows: Supply of materials, tools and manpower to install aluminum windows (frames of minimum 60 mm width). The price of works includes anti-insects wire mesh, handles, windows stopper , crystal clear class 4mm thickness, and repairing the window edges from both sides. All needed work to complete the job will be included within the price. | m² | 1
143 | Wooden Windows (New works): Provision of materials, labour and equipment and all other necessary activities that are required for the installation of wooden windows frames made from Teak wood include teak painting and varnish painting, include 4mm clear glass. Windows frame measurements to be checked onsite. All windows to be side hung and inward opening unless specified otherwise. All glazing works shall be conpleted according to instructions of supervising Engineer. | m² | 1
144 | Repair Steel Windows: Supply of materials, tools and manpower to repair damaged steel windows. Including anti-insects wire mesh, hinges, handles, welding of damaged parts, cleaning the rust stains and removing the old paint before painting with two (2) layers of anti-rust and three (3) layers of oil paint, then providing clear glass of 4mm with new paste. All needed works to complete the job should be included within the cost.. | no. | 1
145 | Repair PVC Windows: Supply of materials, tools, machineries and manpower to repair the damaged PVC windows, including anti-insects wire mesh for openable parts and handle, crystal clear glass (4mm) and repairing the window edges from both sides. All needed works to complete the job, will be included within the price. | no. | 1
146 | Crystal clear glass 4mm: Supply of materials, tools and manpower to remove the damaged glass and paste and to install new crystal clear glass 4 mm with new paste, dumping of all debris to a site approved by local authorities. All needed work to complete the job will be included within the price. | m² | 1
147 | Crystal clear glass 6mm: Supply of materials, tools and manpower to remove the damaged glass and paste and to install new crystal clear glass 6 mm with new paste, dumping of all debris to a site approved by local authorities. All needed work to complete the job will be included within the price. | m² | 1
148 | Reflective-glass 4mm: Supply of materials, tools and manpower to remove the damaged glass and paste and to install new reflective glass 4 mm with new paste, dumping of all debris to a site approved by local authorities.selection of colors of glass according to the instruction of the supervision engineer. All needed work to complete the job will be included within the price. | m² | 1
149 | Obscure"مشجر"-glass 4mm: Supply of materials, tools and manpower to remove the damaged glass and paste and to install new Obscure glass 4 mm with new paste, dumping of all debris to a site approved by local authorities.selection of colors of glass according to the instruction of the supervision engineer. All needed work to complete the job will be included within the price. | m² | 1
150 | Windows Burglar: Supply of materials, tools and manpower to make steel burglar for the windows using 12mm square steel bar every 15cm and the outer frame of angle section 50x50x2mm. The price of works includes anti rust panting , two layers of oil painting and repairing the windows Burglar edges from both sides. All needed work to complete the job will be included within the price. See attached drawing.SEE ATTACHED DRAWING #44. | m² | 1
151 | Steel Lintels (NEW WORKS) Provision of materials, labour and equipment and all requirements to complete the works. The price will include the installation of 2 levelled angle steel sections (size 2.5"x2.5"x4 mm), as lintel above the doors and windows, extending at least 25cm on each side of the openings, welded together by min. 3 iron bars corresponding to the width of the wall and covered by iron mesh. The steel sections will be painted with an anti-rust coat primer produce in Iraq, in accordance to the instructions of the supervising Engineer. | m.l | 1
152 | Window Expanded Metal Mesh (Diamond Shape): Supply of materials, tools and manpower to install diamond shape window expanded metal sheet (opening length= 25mm, width= 30mm and plate thickness= 1.8 mm). The price includes providing steel frame of steel angle 40x40x3mm and internal bracing of steel tube 25x25x2mm every 50cm(both horizontal and vertical), painting with anti- rust paint and three layers of oil paint. All needed work to complete the job will be included within the price. | m² | 1
Stair and Handrial
153 | Steel stair with handrail Supplying materials, tools and manpower for installation the steel stair dimensions of steps (L 1m x W 0.3m)made of from steel chaker plate thickness 2mm,the support frame sides mede of double tube (10*5*0.3)cm ,The work includes handrail hight 0.9m using steel tube squaer section (2*2) inch thickness 2mm as frame the internal tube steel squer (1*1) inch@18cm thickness 2mm with column squaer section 2.5 inch thickness 2mm at the beginning, turning and at the ends,The price of works includes anti rust panting and two layers of oil painting ,All needed work to complete the job will be included within the price."SEE ATTACHED DRAWING #12. | m.l | 1
154 | Steel Handrail: Supply of materials, tools and manpower to install steel handrail (0.9m hight)for staircases, using steel tube squaer section (2*2) inch thickness 2mm as frame the internal tube steel squer (1*1) inch@18cm thickness 2mm with column squaer section 2.5 inch thickness 2mm @ first-End or @ 5m thickness 2mm or according to the approved sample. The price includes anti rust and three layers of oil painting . All needed work to complete the job will be included within the price. | m.l | 1
155 | Steel Handrail-Heritage Shape: Supply of materials, tools and manpower to install steel handrail for staircases hight 0.9m, using steel tube squaer section 40x40x1.8mm as frame the internal steel bar squaer 12mm@18cm thickness 2mm with uesing plate width 10mm thickness 2mm. The price includes anti rust and three layers of oil painting . All needed work to complete the job will be included within the price.SEE ATTACHED DRAWING #49. | m.l | 1
156 | steel stair with handrail--Heritage Shape: Supplying materials, tools and manpower for installation the steel stair dimensions of steps (L 0.9m x W 0.3m)made of from steel chaker plate thickness 3mm,the support frame sides mede of double tube (8*4*0.3)cm ,The work includes handrail hight 0.9musing steel tube squaer section 40x40x1.8mm as frame the internal steel bar squaer 12mm@18cm thickness 2mm with uesing plate width 10mm thickness 2mm,The price of works includes anti rust panting and two layers of oil painting ,All needed work to complete the job will be included within the price."SEE ATTACHED DRAWING #49. | m.l | 1
157 | Repair steel Handrail: Supply of materials, tools, machineries and manpower to repair the damaged Handrail. Price of works shall include oil painting and accessories. All needed work to complete the job will be included within the price.. | m.l | 1
158 | Aluminum Handrails: Supplying and installation of aluminum handrails (height of 90cm) with all accessories. The price includes removing the old steel handrails and providing bigger column sections at the beginning, turning and at the ends. All needed work to complete the job will be included within the price. See attached annex. | m.l | 1
159 | Glass-Aluminum Handrails: Supply of materials, tools and manpower to install glassed aluminum handrails (height 100cm) using tempered glass (security glass) railing 10mm thickness, aluminum tubes and all needed accessories. The price includes removing the old steel handrails and providing bigger column sections at the beginning, turning and at the ends. All needed work to complete the job will be included within the price. See attached annex. | m.l | 1
160 | Steel Stair Handrail Hand Support Railing-pipe Round: Supply of materials, tools and manpower to install Steel Stair Handrail Hand Support Railing-pipe Round dimeter 4.5 cm thickness 2 mm galvanized steel ,non-slip,the work include fixing on wall by brackets and screws each 1.2 m. The price includes anti rust and three layers of oil painting with 3 layers of oil.All needed work to complete the job will be included within the price. | m.l | 1
161 | Emergency steel stair circular (width of step 0.9 m length of stair L m hight H m): Supply of materials, tools, machineries and manpower to installation the Emergency steel stair circular. The price includes: 1-Excavation for the column footing (60x60x60cm). 2-Providing (4) anchor bolts of Ø16mm and length of (40cm) for column. 3-Casting concrete (C25MPA) with Providing and installing base plate of (250x250x10mm) for column. 4-Providing column of steel circular tube Diameter 200mm thicknees 5mm with height H m 5-steps use checker plate thickness 2mm, riser H-18 cm. 6-handrial of circular stair use main circular steel tube D 4 cm thicknees 2mm and sub main steel tube rect. section 4cm x 2cm thicknees 2mm @15cm C/C. 7-the work include good fixing with walls and floor by bars and good welding All works in accordance to the instructions of the supervising Engineer. 8-Painting the whole structure with (2) two-layers of anti rust paint and (3) three-layers of oil paint. specifications, in case it is needed, as well as all needed works to complete the job. SEE ATTACHED DRAWING#14. | m.l | 1
162 | Repair Emergency steel stair circular (width of step W m length of stair L m hight H m): Supply of materials, tools, machineries and manpower to repair the steel stair by reblace the damege parts and welding any weak point,the work include supply new steps checker plate type matching with old steps of stair to compensate the missing steps,remove the any uninform part useing for fixing from bottom and fixing the column of stair with floor by use base plate fixing it by (4) anchor bolts and welding.remove steel rust by cleaning all stair through use Wire Brush,the Price include should be paint one-layer inti-corrosion and two layers oil. All needed work to complete the job will be included within the price. | m.l | 1
163 | Steel Ladder for rooftop: Supply of materials, tools and manpower to fabricate and install (60 cm width) vertical steel ladder by using square steel pipe (50x50x3mm) with protection ring using steel plate (50x3) mm and fixing with the floor by using steel plate 4mm, anchor bolts and screws. The work includes clean all existing steel from rust and dust before painting with two (2) layers using anti-rust and three (3) layers oil paint. All needed works to complete the job will be included within the price. SEE ATTACHED DRAWING#30. | m.l | 1
164 | Steel Cover for opening of drainage: Supply of materials, tools and manpower to install Steel Cover drainage for closed sewrage path, using steel angle 1.5 inch thickness 4mm . The price includes anti rust and three layers of oil painting with 3 layers of oil. All needed work to complete the job will be included within the price. | m² | 1
Partitions
165 | Crystal clear Tempered glass Partitions 10 mm: Supply of materials, tools and manpower for installing crystal clear glass partitions (height according to the drawings and instruction of the engineer) including glass door (1.0x2.0m). The price of works includes tempered glass sheets 10 mm, door locks, handles, hinges and windows for clean the glass and for ventilation according to the instruction of the engineer.the work include use steel frame(square section 4cmx4cmx2mm) for support the glass partitions when the area more than 6 m² and according to the instruction of the engineer. All needed work to complete the job will be included within the price." | m² | 1
166 | Gypsum Partitions Supply of materials, tools and manpower for installing Gypsum Partitions (height according to the instruction of the engineer) .the work include structure manufacture from steel square tube (4cmx4cmx2mm) in two direction(in vertical direction @1.2 m and in horizantal direction @0.6m). The price of works includes covered double face of frame by Gypsum sheets(W 1.2mx H2.4mx t 1cm) fixing it by screws,The price includes the use mesh and polishing by Gypsum plastering for joints and screws,The price of work shall include painting with 3 layers Emulsion paint. the work including pvc door (1.0x2.0m) and opening part door locks with steel frame, handles, hinges, frosted glass 4mm,plastic Skirting 10cm along the partition from bottom, and Remove the existing partion if any. All needed work to complete the job will be included within the price."See attached drawings#13. | m² | 1
167 | PVC Partitions: Supply of materials, tools and manpower for installing PVC partitions (height according to the instruction of the engineer) including doors (1.0x2.0m) and opening part.the work include use steel square tube (4cmx4cmx2mm) in two direction in case increase the area of partition more than 2.5m*2.5m. The price of works includes PVC sheets, door locks, handles, hinges, frosted glass 4mm, and Remove the existing partion if any. All needed work to complete the job will be included within the price." | m² | 1
168 | Composite partitions -(Gypsum Partitions & glass Partitions): Supply of materials, tools and manpower for installing composite Gypsum-glass Partitions (height according to the instruction of the engineer) .the work include constructed using galvanized steel C stud of (0.9 mm thickness and10 cm width) as framework @ 410mm c/c and the frame include using C-section horizontaly and vertically, and fixed with two layers of 10mm tapered edge gypsum plaster board on both side of the metal Framework.uisng dry wall screws, jointed and finished with requisite filler, paper tape, finisher and primer suitable for gypsum plaster boards. The price also inlcude installing aluminum window (4 mm glass thickness) up to the false ceiling. The price inlcude the metal skeleton use steel square tube (10cmx5cmx1.8mm) necessary to support windows and gypsum board partition. The price also include painting the whole steel frame with 2 layers of anti-rust, and 2 layers of oil painting using spray machine. The metal must be fixed to the concrete roof to ensure the rigidity of the structure. All needed works to complete the job should be included within the cost. All work must be done according to the supervising engineer's instructions. | m² | 1
169 | Steel Partitions for close any area (wxH): Supply of materials, tools and manpower to install Steel Partitions (wxH) for closed area , using main steel square tube (4cmx4cmx2mm)on perimeterof area and use steel angle 1.5 inch thickness 3mm in two direction @20cm for internal members . the work including steel door (1x2m) same as details of Partitions and opening part door locks with steel frame, handles, hinges.the work include install crystal clear class 4mm thickness with paste for all partitions.The price includes anti rust and three layers of oil painting with 3 layers of oil. All needed work to complete the job will be included within the price. | m² | 1
170 | Theatre Hall Wall Finish (Sound Proof) Supply of materials, tools, and manpower to install accoustic and sound proof panels (Noise stop Acoustic Panel Specifications Panel thickness 22.5mm. Fire rating 30 minutes. Noise reduction 49dB. Composition of the Noise stop Acoustic Panel 22.5mm. 12.5mm soundblock plasterboard, tapered edge. 5kg/m² mass loaded vinyl barrier mat, soundproofing qualities. 5mm acoustic grade closed-cell foam. 5kg/m² mass loaded vinyl barrier mat, soundproofing qualities.). The price include cutting, plastering, gluing and all necessary work to have the work complete. | m² | 1
Constraction activities-to support the persons with disabilities
171 | Concrete Ramp : Supply of materials, tools and manpower to cast concrete ramp for persons with disabilities dimensions (L X Width :1.2 x H m), according to the specification, the slop of ramp between (1:12 -1:20 max),the shape of ramp on L or U with work landing.The work includes steps as below: 1- build the sides of ramp by solid blocks (40x20x15 cm) to support the ramp thickness of wall 20cm with cement plastering 20mm for external fases. 2- backfilling the space between the sides wall, using subbase materials from natural sources free from clay, silt, or any or organic materials. Backfilling material shall be applied on layers of (20-25) cm thickness, watered, and compacted. 3- casting (10cm ) concrete with BRC(200x200x5mm) using sulphate resistant cement for (C25MPa) concrete. 4- install steel handrail for staircases, using steel tube squaer section (2*2) inch thickness 2mm as frame the internal tube steel squer (1*1) inch@18cm thickness 2mm with column squaer section 3 inch @ first-End or @ 5m thickness 2mm or according to the approved sample. The price includes anti rust and three layers of oil painting from two side,in case the ramp supported to wall from one side useing Steel Stair Handrail Hand Support Railing-pipe Round dimeter 6 cm thickness 2 mm galvanized steel ,non-slip,the work include fixing on wall by brackets and screws each 1.2 m. The price includes anti rust and three layers of oil painting with 3 layers of oil replase steel handrial. , All needed works to complete the job, will be included within the price. SEE ATTACHED DRAWING#32. | m.l | 1
172 | Steel Ramp: Supply of materials, tools and manpower to instllation steel frame ramp for persons with disabilities dimensions (L X Width :1.2 x H m), according to the specification, the slop of ramp between (1:12 -1:20 max),the shape of ramp on L or U with work landing.The work includes steps as below: 1-Excavation for the columns footing (60x60x60cm). 2-Providing (4) anchor bolts of Ø16mm and length of (40cm) for each column. 3-Casting concrete (C25MPA) with Providing and installing base plate of (250x250x10mm) for each column. 4-Providing columns of steel square tube 100x100x3mm with height according the slop. 5-use main steel beam using section 100x100x3mm to be fixed between all columns for both directions. 6-Steel Purlin using rectangular steel section 100x50x3mm and spaced 60 cm c/c. 7-covering the floor of ramp by checker plate sheet thickness 2 mm, fixed by screws. 8-install steel handrail for staircases, using steel tube squaer section (2*2) inch thickness 2mm as frame the internal tube steel squer (1*1) inch@18cm thickness 2mm or according to the approved sample. The price includes anti rust and three layers of oil painting from two side,in case the ramp supported to wall from one side useing Steel Stair Handrail Hand Support Railing-pipe Round dimeter 6 cm thickness 2 mm galvanized steel ,non-slip,the work include fixing on wall by brackets and screws each 1.2 m. 8-closed the two side by steel plate gauge 18(1.41mm). 8-Painting the whole structure with (2) two-layers of anti rust paint and (3) three-layers of oil paint.in case it is needed, as well as all needed works to complete the job. | m.l | 1
Sewerage works
173 | Manholes and Gullies replacement: Supply of materials,tools, and manpower to demolish the cracking work of concrete and asphalt of (Manholes and Gullies) and everything that interferes with the work and to remove the base of the old cover of manholes and gullies, and deliver it to the enduser stores, and to install the new manhole base using concrete with the addition of special materials to accelerate the hardening process, and with levelling of the manholes covers with the street level, with wellding works if needed, and with continuous spraying with water until the concrete has completely solidified, and the price includes all that the work requires from lifting the rubble and transporting it to the landfill sites designated for it, with the use warning signs and warning tapes for the work sites. All works according to the supervisior engineer.
a | Manholes | no. | 1
b | Gullies | no. | 1
174 | Maintenance of sewerage pipes: Supply of materials, machine and manpower to clean the sewerage pipes net starting from the toilets, manholes to the main septic tank using high pressure air/water. The work includes replace the damaged manhole covers and others with new one. All needed work to complete the job will be included within the price. | m.l | 1
175 | Manholes: Supply and install Plastic Manholes of various diameters and to any depth,durable type of plastic (Polypropylene) that is resistant to oils and chemical substances. plastic manholes have a solid structure with input and output connections on all four sides. Price to include excavation, backfilling, benching, rubber gasket at inlets and outlets, installation plastic cover. All needed work to complete the job will be included within the price.
a | 80x80 cm | no. | 1
b | 60x60 cm | no. | 1
c | 40x40 cm | no. | 1
d | 30x30 cm | no. | 1
e | 20x20 cm | no. | 1
f | circular 70x40 cm | no. | 1
g | circular 50x40 cm | no. | 1
h | circular 50x30 cm | no. | 1
176 | Manholes 50x50cm: Supply of materials, tools and manpower to build the external manhole using solid concrete blocks and cement mortar with cement plastering from inside and outside using cement-sand mortar (1:3). The work includes excavation, casting 15cm concrete (C20Mpa) using sulphate resistant cement, installation of cast iron manhole cover of (40x40)cm. All needed work to complete the job will be included within the price.See attached drawing #43. | no. | 1
177 | Water network repairing: Supplying of materials, tools and manpower to inspect and repair the water network pipes (Hot & Cool) by replacing damaged pipes. Including pipe fittings, connections and accessories. All needed works to complete the job should be included within the cost. | m.l | 1
178 | Drain pipes (roof Drain): Supply of materials, tools and manpower to remove damaged water drain and install new galvanized steel pipe 101mm (4") with all connections and accessories to fix with the roof and wall. All needed works to complete the job should be included within the cost. | m.l | 1
179 | PVC Drain pipes: Supply of materials, tools and manpower to remove the damaged water roof drain pipes and install new PVC pipes . Including all connections and needed accessories to fix on roof and walls. All needed work to complete the job will be included within the price.
a | 2.5" | m.l | 1
b | 4" | m.l | 1
180 | Eastern toilet: Supply of materials, tools and manpower to remove the damaged eastern toilet pan and to install new ceramic eastern toilet. Including siphon(flush tank), gully trap Ø100mm (4"), flexible hose and water connections. All needed work to complete the job will be included within the price. | no. | 1
181 | Siphon (Flush Tank): Supply of materials, tools and manpower to install siphon, valves and all needed accessories for completing water connections. All needed works to complete the job should be included within the cost. | no. | 1
182 | Western toilet: Supply of materials, tools and manpower to remove the damaged western toilet pan and to install new ceramic western toilet. Including siphon(flush tank), gully trap Ø100mm (4"), flexible hose and water connections. All needed work to complete the job will be included within the price. | no. | 1
183 | Western toilet for persons with disability: Supply of materials, tools and manpower to remove the damaged western toilet pan and to install new ceramic western toilet. Including siphon(flush tank), gully trap Ø100mm (4"), flexible hose and water connections,the work include installation support members stainless steel for persons with disability,siphon and bidet sprayer. All needed work to complete the job will be included within the price. | no. | 1
184 | Bath Shower Mixer taps: Supply of materials, tools and manpower to install bath shower mixer taps and needed accessories for completing water connections with main water supply pipes for cold and hot water. All needed works to complete the job should be included within the cost. | no. | 1
185 | Ceramic Shower (80x80cm): Supply of materials, tools and manpower to remove the damaged ceramic shower base and install new ceramic shower (80x80cm), including fixed shower head with mixer taps, locks valves and all needed accessories with complete water connections. All needed works to complete the job, shall be included within the price. | no. | 1
186 | Ceramic wash basin: Supply of materials, tools and manpower to install ceramic wash basin with stand, mixer taps, valves, mirror(60x50)cm and all fittings with complete water connections. All needed work to complete the job will be included within the price. | no. | 1
187 | Multiple Wash Basins with Three Water Mixer for (WC) Supply material, manpower and tools to install multiple washing basins (Three Wash Basins) installed on Granite base with stand and three water mixer and all other accessories.must be the brand original manufacturing. The price includes supplying of material, tools and manpower for all necessary plumbing (water supply and draining) to have it fully functional. All works should be done according to the instructions of the supervising engineer. | No. | 1
188 | Mixer taps: Supply of materials, tools and manpower to install mixer taps and all needed accessories for completing water connections. All needed works to complete the job should be included within the cost. | no. | 1
189 | Shower head and mixer taps: Supply of materials, tools and manpower to install mixer taps with shower head. The price of works includes all needed fittings. All needed work to complete the job will be included within the price. | no. | 1
190 | Special Ceramic Wash Basin: (For Handicapped People) Supply of materials , tools and manpower to install special ceramic wash basin for handicapped people. The price includes single handle chrome mixer, valves, flexible hoses for water connections and all fittings with complete water connections, also special outlet fittings and connection to the nearest floor drain . All needed work to complete the job will be included within the price. | no. | 1
191 | Grab Bar (Handle): (For Handicapped People) Supply of materials , tools and manpower to install stainless teel grab bar (handle) according to the following specs: 1-Ø=38mm. 2-Length= 40-60cm. 3-Average weight= 800-1000 grams. All needed work to complete the job will be included within the price. See attached drawing. | no. | 1
192 | Taps: Supply of materials, tools and manpower to connect chrome water taps. Price of the work shall include water connections. All needed work to complete the job will be included within the price. | no. | 1
a | size 1/2" | no. | 1
b | size 3/4" | no. | 1
193 | Water Hose Supply of materials, tools, and manpower to install water hose of 3/4' size length 20m connected to the water tap. Price of the work shall include water connections. All needed work to complete the job will be included within the price. | no. | 1
194 | Roof Drain Gutter: Supply of materials, tools and manpower to install roof drain gutter (40x30)cm on both sides of the sheds using galvanize plate gauge 18 (1.41mm). The price includes installing galvanized iron pipe for roof drain and fittings same as existing. All needed work to complete | m.l | 1
195 | Main water supply PPR pipeline: Supply of materials, tools and manpower remove the damaged main supply water pipeline and installing new PPR water pipeline as diameter 1" (25.4mm). Including excavation (W30xDepth 30cm), pipe fittings, demolishing, concrete works, cement plastering, all required connections, accessories, pressure test applied as 5 bar for 6 hours for the whole pipe, connections between the tanks on the roof, concreting 10 cm around the pipes and backfilling. All needed works to complete the job will be included within the price. | m.l | 1
196 | Electrical boiler: Supplying, installing , connect and commissioning of electrical heater with the below capacity, and power with complete fittings & accessories connecting with (2x4mm²) PVC cable and 20A switch. The price includes supplying, installing, testing, commissioning with all accessories to complete work as required
a | 60 liter, with 100 watt. | no. | 1
b | 150 liter, with 150 watt. | no. | 1
c | 200 liter, with 200 watt | no. | 1
d | 300 liter, with 300 watt | no. | 1
197 | Water Pump: Supplying materials , tools and manpower to install, connect and commissioning water pump of capacity( hp) including all required water pipe connections using 3/4 inch PPR pipe, electrical connections using 1.0kV grade 2x2.5 sq.mm and outdoor waterproof type, with socket switch, with providing galvanized protective metal frame cage to cover the pump & accessories and all other requirements to complete a good work.
a | 0.5 hp | no. | 1
b | 1 hp | no. | 1
c | 2 hp | no. | 1
Water Tanks
198 | Water tank (galvanized): Supply of materials, tools and manpower for installing galvanized water tank. with cylindrical shape and with plate gauge 16(1.56mm), supported by steel base made with 50mm (2") angle shape, including the connection of the inlet and outlet pipes. The price of work includes all piping and fittings, valves, float valves, accessories. All needed work to complete the job will be included within the price.
a | 1000 liter | no. | 1
b | 1200 liter | no. | 1
c | 1400 liter | no. | 1
d | 2000 liter | no. | 1
e | 5000 liter | no. | 1
199 | Water Tank steel Base manfucturing and Supply of Iron water tank base 1.05×1.05m , clear height 1.75m , made from Iron Angle L 2×2 Inches, thickness 3 mm for all base ,smooth ,Turkish Iron, four legs with bracing cross Angle from two sides with bracing bottom for four sides to prevent buckling, with four Iron angle at the top corner of base with four Iron Angle at the top to be base of water tank,With iron Angle at the top-Middle of base , good welding for all sides of contacting.the price should be including Anti-rust paint two layers and all needs to complete the job should be within the price under supervision of Ta'afi Engineers. | no. | 1
200 | Water tank (Polyethlene): Supply of materials, tools and manpower for installing polyethylene water tank. with cylindrical shape, and including the connection of the inlet and outlet pipes. The price of work includes all piping and fittings, valves, float valves, accessories. All needed work to complete the job will be included within the price.
a | 1000 liter | no. | 1
b | 1500 liter | no. | 1
c | 2000 liter | no. | 1
d | 5000 liter | no. | 1
201 | Water tank (galvanized)-Bolts system: Supply of materials, tools and manpower for installing galvanized water tank Bolts system with rectangular shape and with plate gauge 16(1.56mm), use panels (1.22x1.22m)connected by bolts and nuts,the work include support the tank from internal by roof support carrier and internal Tie road,the price include installation plastic base under water tank the supported by steel base made with 50mm (2") angle shape, including the connection of the inlet and outlet pipes. The price of work includes all piping and fittings, valves, float valves, ladder,accessories. All needed work to complete the job will be included within the price. | m³ | 1
202 | CPVC Pipes: Supply and install CPVC pipes for cold and hot water pipes(16 bar) The price includes other fittings as per drawings and specifications.
a | 14 mm | m.l | 1
b | 20 mm | m.l | 1
c | 25 mm | m.l | 1
d | 32 mm | m.l | 1
e | 40 mm | m.l | 1
f | 50 mm | m.l | 1
g | 63 mm | m.l | 1
h | 63 mm | m.l | 1
i | 75 mm | m.l | 1
j | 110 mm | m.l | 1
203 | Septic Tank: Supply of materials, tools and manpower to constrcution a septic tank of internal dimension (L, W and H). The price includes: 1-Soil excavations in any types of soil. 2-Provide a layer of crushed stones 10cm under the foundation concrete. 3-Casting (25cm) Rineforced concrete for the foundation using (C25Mpa) Concrete and using sulphate resistant cement,Rinforcement 4Ø12mm and stirrups Ø10mm @30cm c/c. 4-Build the walls of 40 cm width with solid blocks (15x20x40cm) and cement mortar (1:3). 5-Casting reinforced concrete slab (20cm) with two layers of 12mmØ spaced @20cm both directions. 6-Installation of manhole steel cover of (40 x 40 )cm. 7-Plastering of the interior walls with two layers of cement plastering 20mm thickness. The price includes a layer of cement splash dash. All needed work to complete the job will be included within the price.
a | internal dimension (L=2.0m, W=2.0m and H=2.2m) | no. | 1
b | internal dimension (L=3.0m, W=2.0m and H=2.5m) | no. | 1
Furniture
204 | Curtain: Supply and install windows blinds (curtains) with all needed to complete work from good origin and good type. | m² | 1
205 | Roll of Floor Mat Carpet Supply of floor mat carpet 5mm thickness,( W×L)m for each roll carpet, wool-linen yarn, odourless and suitable for all floor types, Solid color carpet, Texture, all edge of carpet sould be sewing with suitable string in color and strength and all needs to complete the job should be within the price under supervision Engineer. | m² | 1
206 | Steel dumpster containers (16 m³) Supply good quality dumpster container 16m³, to be towing by municipality machine (sample should be tested approved by municipality and supervision engineer) with below specification:1-dimension(according to attached drawings and photo) :(A-199cm Height including the Wheel.B-228cm width.C-528 cm length )2-technical specification (A-chassis (I section 8inch steel bar, 5.28-meter length), dumpster base plate 5mm thickness,B-front sides plate 4mm thickness surrounding with 8 mm plate thickness reinforcement with C channel 8 inches 7.5 m length, lifting base is C channel 8 inches with heavy-duty hook 60 mm thickness upside down u shape 41.1cm length, fixing with 16mm plate (according to attached drawings.C-back side reinforcement with 5mm thick iron plate upside down u shape.D-roof plate 4mm thickness surrounding with upside-down u shape 6 mm thickness iron plate welding with the roof and the sides 3surrounding plate along with the container with an opening to through the garbage inside the dumpster 4 opening each side ( Total 8 opening) dimension 85cm*69cm with the installation of doors 3mm iron plate with 2 hinges good quality, open to outside.E-back door 4mm thickness reinforcement with 4mm thickness plate, with arms for opening.F-iron wheel to facilitate bin Sliding during the lifting process (4 iron wheel) The back wheel is 30 cm in length and 20cm in length the front wheel, is 15cm in diameter, 6mm thickness fixed by 16mm iron plate support on each side to avoid damage during lifting.G-painting with 2 layers of anti-rust paint and 3 layers of oil paint (color to be determined by supervision engineers and municipality ). H-the price includes delivering the dumpster container to the GPS's. See attached drawing #33. | no. | 1
207 | Stainless Steel water cooler: Supplying, installing, commissioning stainless steel electrical water-cooler with three taps (150liters), water connections includes wiring/connecting with 1.0 kV grade 2*2.5mm² PVC insulated copper cable/wires laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (20 mm dia) with all accessories. The price includes supplying,installing,connecting,laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
208 | Kitchen Sink: Supply, install and commissioning stainless steel kitchen sink 50CM*60CM, complete with chrome plated mixer for kitchen sinks c/w hand spray set and retractable hose, supports, waste outlet, tail piece, PVC P-trap, as per drawingsand specifications..
a | single bowl | no. | 1
b | duple bowl | no. | 1
209 | Fire Extinguisher Supplying, installing, Fire extinguisher with weight (W) kg and type (dry powder),good brand and with good quality.
a | 6 kg | no. | 1
b | 12 kg | no. | 1
Shelves
210 | Shelves Supplying and installing shelves for shops and library as below
a | with a width of (20-30) cm with all needed to complete work from good brand and good quality. | m.l | 1
b | Supply of materials, tools, and manpower to install aluminum bookshelves of 3 m height and 0.6m depth (Double Faced). aluminum thickness is 3mm. The price includes all accessories to have the work complete. All works should be done according to the instructions of the supervising engineer. | m.l | 1
Park works
211 | Trash Basket: Supply and install new waste bin, 60l size and the models according to the needed. | no. | 1
212 | Garbage Bin Supply of Plastic outdoor garbage bin 100 liter, with 2PCs rubber wheels and opening top cover, weight not less 6kg. | no. | 1
213 | Benches and Tables (Outdoor):
a | Supply of materials, tools, and manpower to supply and install wooden benches, as per the supervising engineer instructions. The bench dimentions are 1.8m * 0.6m. The wood sit on a metal structure. | no. | 1
b | Benches with Canopy Supply of materials, tools, and manpower to supply and install wooden benches with synthetic leather canopy as per the supervising engineer instructions. The bench dimentions are 1.8m * 0.5m. The wood sit on a metal structure and that structure carry the synthetic leather canopy. | no. | 1
c | Fixed Wooden Tables Supply of materials, tools, and manpower to supply and install wooden benches in the places shown in the drawings. The wood used must be treated with sandpaper of 500 grit and painted multiple times with a paint that ressist UV rays, water and external conditions. | no. | 1
214 | Playgrounds slids for children: Supplying and installing a Playgrounds slids for children placed in parks. All the needed works to complete the job shall be included within the price. | no. | 1
215 | children's jumping toys: Supplying and installing good quality children's jumping toys that placed in garden,approve on the samples according to supervisor engineer. All the needed works to complete the job shall be included within the price. | no. | 1
216 | Triple Steel metal swings: Supplying and installing a triple swings, with dimensions 323 x 205x 2cm. The 3 Swing Set includes adjustable ropes and plastic seats that will In addition to the structure. | no. | 1
Technical Systems work
217 | Security CCTV System: Supply, install, test and commission of security CCTV system including the following items. The price includes supplying, installing, connecting, cables, conduits with all necessary required accessories necessary cutting, drilling, testing, and commissioning to complete works with all accessories as required.
a | 8 Channel Digital Video Recorder 480 FPS Recording, 2TB HDD. | no. | 1
b | 16 Channel Digital Video Recorder 480 FPS Recording, 2TB HDD. | no. | 1
c | 32 Channel Digital Video Recorder 480 FPS Recording, 8TB HDD. | no. | 1
d | Indoor Camera, day and night, full HD, 8mm. | no. | 1
e | Outdoor Camera, day and night, full HD, 8mm. | no. | 1
f | Dome CCTV | no. | 1
g | Bullet CCTV | no. | 1
h | C-Mount CCTV | no. | 1
i | PTZ Pan-tilt CCTV | no. | 1
j | Day/Night CCTV | no. | 1
k | Infrared CCTV | no. | 1
l | IP CCTV | no. | 1
m | Wireless CCTV | no. | 1
n | HD CCTV | no. | 1
o | UPS Power Backup for Security Camera System 1500VA. | no. | 1
p | AC230V PSU in indoor/outdoor junction box. | no. | 1
q | 8 Channel Network Video Recorder 480 FPS Recording, 2TB HDD. | no. | 1
r | 16 Channel Network Video Recorder 480 FPS Recording, 2TB HDD. | no. | 1
s | 32 Channel Network Video Recorder 480 FPS Recording, 8TB HDD. | no. | 1
t | Power Over Ethernet Switch POE 8 ports. | no. | 1
v | Power Over Ethernet Switch POE 16 ports. | no. | 1
u | Power Over Ethernet Switch POE 32 ports. | no. | 1
w | Motion sensor: Supply, tools, materials, and manpower to install LED VALUE PIR Motion Sensor - Wall Mounted, Sensors with infrared technology with below specs: − 180° motion sensor (passive infrared technology) − Wall surface mounting − Timer function − Photocell detector available for daylight detection − Input voltage: 220…240 V AC − Operating frequency: 50/60 Hz − Ambient temperature in operation: -20- +45 °C. − Panels − Alarm system, sound, SMS alert.
218 | Sound System: Supply, install & test sound system includes wiring with electrolytic touch pitch (ETP) copper wire laid through PVC conduit pipe) with all other accessories such as :(1No.) of mixer and amplifier power O/P =250 watt, power source 100-240 V, S/N ratio< 300m frequency response 5 Hz-50 KHz and (20No.) of ceiling loud speaker-recessed ceiling mounted type 10Watt and (4No) of MIC input with all necessary accessories .The price include supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
219 | Sound System for the theater: Supplying, installing and testing of Sound System for the theater which include (but not limited to): - Ceiling mount Speakers. - Speaker selector switch box. - Digital Audio Mixer / Feedback reducer/ Amplifier. - Receivers. - Handheld Cardioid Dynamic Microphone. - Omnidirectional Head worn Microphone. - lavalier microphone. - Unpack Transmitter. - Disc player/recorder. - Teak wood cabinet for equipment. The capacity of the speakers is calculated according to the room area and the mics according to the specifications required by the theater hall and the supplier shall submit catalogs for specifications of the system for the approval by the site engineer. The price includes supplying, designing(as per the requirement ), installing, connecting, necessary cutting, drilling, testing, and commissioning with all accessories to complete work as required. | no. | 1
Communication works
220 | Main distribution frame (MDF): Supply, install and connect a main distribution frame (MDF) for 300 lines with a lock, including riser cables for connections between (MDF) and intermediate distribution frames (IDF's). The price includes supplying, installing, laying, connecting, necessary cutting, drilling, testing, and commissioning with all accessories to complete works as required. | no. | 1
221 | Wall jack outlet (telephone) : Supply, install, connect and commission hidden wall phone jack outlet (RJ11) includes wiring with 4x0.6mm² PVC insulated copper wire laid through conceal PVC conduit (Dia 20 mm) pipe (inside the wall from the (SPF) to the building rooms. The price include supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
222 | Telephone Cable: Supply, install, connect and commission of telephone cable with size 30 pairs (2*0.5)mm each laid inside PVC pipe or over cable Tray from main distribution Frame (MDF) to sub distribution Frame (IDF) with all accessories. The price include supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | m.l | 1
223 | Wall jack outlet(Network) : Supply, install, connect and commission Internet outlet (RJ45) by using UTP CAT6 cables in 25 mm dia. PVC pipes include all available materials, Internet sockets, boxes, junctions. The price include supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
224 | Sub (Intermediate ) distribution frame (IDF) : Supply, install and connect a Sub distribution frame(IDF) for 50 lines with a lock . The price include supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
225 | Linksys switch: Supply, install, connect and commission of Linksys 24-10/100 port switch, 110–240V AC, 50/60Hz, wired connection speed up to 1000 Mbps, bandwidth 48 Gbps, easy plug & play connection, compatible or equivalent to Cisco protocols, installing inside a metal Box and lock with all the accessories. The price include supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
226 | Nano station device: Supply, install, connect and commission of Nano station - 2.4 GHZ, Power supply 12V , 16MB RAM, 4MB FLASH, Channel width 5/10/20MHz with all the required accessories. The price include supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
227 | Telecommunication system 1-Telephone Main Distribution Board Supplying, Installation, testing and commissioning of telephone main distribution box (MDF),capacity not less than 50 port with terminal blocks, provided with locker, designated telephone numbers, in prefabricated MS surface complete with all accessories and requirements to operate whole the system properly. 2-Telephone Sub Distribution Frame Supplying, Installation, testing and commissioning of telephone sub distribution box (SDF),capacity not less than 20 port with terminal blocks, provided with locker, written telephone numbers, in prefabricated MS surface complete with all accessories and requirements to operate whole the system properly. 3-Telephone Cable Supplying, Installation, testing and commissioning of telephone cable [(2x0.5mm²)x30], to connect the main distribution box(MDF) to sub distribution boxes(SDF), passing through 20mm dia PVC pipes, cable tray, plastic box and all accessories.The price include supply & installation of wires, PVC pipes, all material, accessories, works(cutting, drilling, repair, painting) and any other to complete the work entirely according to technical specifications. 4-Telephone socket outlet Supplying, Installation, testing and commissioning of telephone socket outlet(RJ11), installed by using (4x0.5mm²) telephone wires inside 20mm dia PVC pipe under wall surface(hidden), at the corridors carried on galvanized metal cable trays, providing junction boxes at the corners, numbering with plastic rings on both ends, plastic box, all outlet sockets to be provided with sticker numbers properly. The price include supply & installation of wires, PVC pipes, accessories, all associated works;(drilling, cutting, repairing, painting,. etc)and any other work to complete and operate the whole system properly according to technical specifications. | LS | 1
228 | Data System 1-LAN: Supplying, Installation, testing and commissioning of LAN network for connecting computers, wiring with cable(UTP Cat6) to complete with all required material to connect the main distribution frame board to sub switches (two lines for each switch) also to connect the sub switches to wall mounted internet socket outlet (RJ45), at rooms and halls installed inside 20mm dia.under wall surface(hidden), at the corridors carried on galvanized metal cable trays, providing junction boxes at the corners, numbering with plastic rings on both ends, plastic box, all outlet sockets to be provided with sticker numbers properly. The price include supply, installation of wires, PVC pipes, all material, associated works;(drilling, cutting, repairing, painting, . etc.) and any other to complete and operate the whole system properly according to technical specifications. 2-Sub Switches: Supplying, Installation, testing and commissioning of sub switches of type (24-10/100 port) (Linksys) compatible with (Cisco protocols) to be distributed inside the building according to prepared sketch, inside prefabricated Aluminium frame with glass lockable complete with all requirements and all accessories.The price include all material, accessories, works(cutting, drilling, repair, painting) and any other to complete the work entirely according to technical specifications. 3-Internet receiver-transmitter: Supplying, Installing, testing and commissioning of internal internet receiver-transmitter of type (Nano station, 2.4GHz), (ubnt or equivalent),complete set with all accessories, to be connected with computer network inside the building(should be compatible with the internet service provider). The price includes supplying, installing, testing and commissioning with all accessories connections and any other requirements to operate the whole system and function properly. | LS | 1
229 | Internet receiver-transmitter: Supplying, Installing, testing and commissioning of internal internet receiver-transmitter of type (Nano station, 2.4GHz), (ubnt or equivalent),complete set with all accessories, to be connected with computer network inside the building( compatible with the internet service provider). The price includes supplying, installing, testing and commissioning with all accessories connections and any other requirements to operate the whole system and function properly. | no. | 1
230 | Digital Signage / Display 75 Inches: Supplying ,Installation, testing and commissioning of Digital Signage / Display of 75" size and Aspect Ratio 16:9 with following specification: 1-Sunlight Readable view full color images and video perfectly in bright sunlight 2-Eye Comfort 100% reflective - no backlight, no blue light emissions, and no flashing. 3- Full HD resolution (1920x1080) and 16.7 million addressable colors. 4- Wide Temp suitable for most climates with a -20°C to +70°C operating temp 5- Refresh Rate 60Hz. 6- Response Time (G to G) 8ms. 7- Operation Hours (Hours / Day) 24/7. 8- Connectivity HDMI, Wifi, USB. 9- Panel Technology IPS. 10- Portrait/Landscape orientation The display is intended for outdoor use and must be water resistant and heat resistant. The price also includes galvanized steel frame to fix the signage. | no. | 1
231 | Sidewalk Stand with signage board (1.5*0.7*0.1 m) Supply of materials, tools, and manpower to install sidewalk stand with signage board. The stand and the frame are galvanized steel and aluminum plate as board (Thickness 2mm). The price includes a concrete base and fixing the stand on the sidewalk. The welding or gluing must be seamless. All needed work to complete the job will be included within the price. | no. | 1
232 | Wall Mounted signage board (1.5*1m) Supply of materials, tools, and manpower to install wall mounted signage board. The frame is made from Aluminum section of 2 mm. The price includes fixing the board on the wall. The welding or gluing must be seamless. All needed work to complete the job will be included in the price. | no. | 1
233 | Wooden umbrella for parks: Supply of materials, tools, and manpower for installing A wooden umbrella for parks, use of wooden columns with a section of 10 x 10 cm with a height of (3-2.5) meters. The number of columns ranges from (6-8) poles according to the area of the wooden umbrella. The columns are covered from the bottom with steel legs. for beams use double rectangular section of 10 x 5 cm on perimeter, then connected 6-beams joists in the center of the canopy to support the roof. The roof consists of wooden panels with a rectangular section of 10 x 1 cm covering the entire ceiling area with protrusions from all directions of 40 cm. The work includes covering the canopy from the top with a cover of moisture-insulating fabric with a drop from the ceiling of 25 cm from all sides. The price includes closing the side spaces between the columns using CNC wood panels and horizontal wooden sections 10 x 3 cm along the entire circumference of the shade 2, vertical wooden sections 10 x 2 cm every 10 cm, with entrance door, the price includes manufacturing seating seats on the inner perimeter of the umbrella, the work includes painting using resistant paint To UV rays and water resistant in the appropriate color, and the wood texture should not hide the paint. It should be on three layers or more. After using fine sandpaper, the final surface must be smooth, free from drip marks. All needed works to complete the job should be included within the cost. All work must be done according to the supervising engineer's instructions. | m² | 1
234 | Covering the External walls by Boardex panel: Supply of materials, tools, and manpower for installing board dex panel for external walls use sheets 1.2mx2.4mx1cm. the work include installation frame using galvanized steel tube square section 1.5-inch thickness 2mm@60 cm C/C in two direction horizontally and vertically, then fixed on it one layer of 10mm boardex panel on external side of the metal Framework. using dry wall screws, jointed and finished with requisite filler, paper tape, finisher, and primer suitable for joints by acrylic putty for exterior walls. the work include paint the exterior walls covering by boardex panel, with three layers of plastic (silicon waterproof) paint. All needed works to complete the job should be included in the cost. All work must be done according to the supervising engineer's instructions. | m² | 1
235 | Extension floor - steel Frame: Supplying materials, tools and manpower for installation the steel frame dimension (LxWxH)m the frame contains main columns square section (10*10*0.2)cm, fixed by bolts welded with base plate thickness 8mm,roof frame is made of main beam (10*10*0.2)cm square black steel tube, the internal beams (10*5*0.2)cm@60cmc/c, the roof shall be 3mm thickness Chaker plate, The price of works includes anti-rust panting and two layers of oil painting ,All needed work to complete the job will be included within the price.
a | steel tube square section (10*10*0.2)cm | m.l | 1
b | steel tube Rect.section (10*5*0.2)cm | m.l | 1
c | Chaker plate thickness 3mm | m² | 1
Football Playground Works
236 | Steel column Pipe circular section diameter 3.5 inch Supply of materials, tools and manpower to Drilling and installing a 3.5-inch diameter pipe thickness 3mm using a well-drilling machine with a depth of 50 cm and a diameter of 35 cm,then casting itusing sulphate resisting cement SRC. The work includes bonding the fram with the concrete foundation of the playground. The price includes anti rust and three layers of oil painting green color with 3 layers of oil. All needed works to complete the job will be included within the price. | m.l | 1
237 | Lateral Steel Pipe circular section diameter 2 inch Supply of materials, tools and manpower to installing a 2-inch diameter pipe thickness 2mm. welding with steel column 3.5 inch about perimeter 4-parallel lines. The work includes bonding the fram with the concrete foundation of the playground. The price includes anti rust and three layers of oil painting green color with 3 layers of oil. All needed works to complete the job will be included within the price. | m.l | 1
238 | BRC Net: Supply of materials, tools and manpower to installing a BRC net of the galvanized type and covered, green color, 4 mm thickness and 4 m hight, with good tension by using a stringing wire with three equal lines around the playground,the price include installing BRC doors according to the instruction of the engineer. All needed works to complete the job will be included within the price. | m² | 1
239 | Crushed Gravel: Supply of materials, tools and manpower to spread a layer of Crushed gravel, the last layer of fine crushed gravel size 8 mm. All needed works to complete the job will be included within the price. | m³ | 1
240 | Artificial Grass/Turf for Playground: Supply of materials, tools and manpower to install Artificial turf flooring for football fields with all its accessories, with fine sand (15 mm) thick and rubber granules Grass density 16 stitches per 10 cm height of Grass 50 mm, using a special truck for the spread of materiales according to the instruction of the supervision engineer. The work includes planning the floor of stad in white color, according to sports specifications. The price include pading, adhesuves, infill and all material and accessoreis to have complete work.All needed work to complete the job will be included within the price. | m² | 1
241 | Protective Rob Net for Football: Supply of materials, tools and manpower to installing a protective net for football with heat and rain resistant specifications, to be attached to the roof of the stadium and descended from the sides of 2m accessoreis to have complete work.All needed work to complete the job will be included within the price. | m² | 1
242 | Truss frame double Pipe: Supply of materials, tools and manpower to Drilling and installing a truss frame double Pipe dimeter of pipe 3 inch thickness 3mm between two pipe distence 40cm for contect two pipe use pipe 2 inch dimeter thickness 3mm@60cm c/c,for execvation using a well-drilling machine with a depth of 50 cm and a diameter of 35 cm,then casting itusing sulphate resisting cement SRC.the price include to be the truss stright as column or curved as beam on ceiling.The work includes bonding the fram with the concrete foundation of the playground.The price includes anti rust and three layers of oil painting green color with 3 layers of oil. All needed works to complete the job will be included within the price. | m.l | 1
243 | Seats of football audience: Supply of materials, tools and manpower to Installing good quality plastic seats for audience on an iron structure made of a rectangular section of 10 x 5 x 0.2 cm on the perimeter. Vertical support is done by using the same steel tube section to work steel frame stairs every 1.2 m, in addition to installing steel bases with a rectangular section (30 x 2 x 0.3 cm) to support the feet of audience and installing plastic seats. plastic seat has dimensions (47 x 41 x 33) cm. The height of the seat from the steel floor is 43 cm., the work incude all accessoreis to have complete work. All needed work to complete the job will be included within the price.see atteched drawing | no. | 1
244 | Plastic Seats for Audience: Supply of materials, tools, and manpower to Installing good quality plastic seats for audience on the concrete base of the playground stairs. plastic seat has dimensions (47 x 41 x 33) cm. The height of the seat from the steel floor is 43 cm., the work includes all accessories to have complete work. All needed work to complete the job will be included in the price. see attached drawing. | no. | 1
245 | Goals with rob nets: Supply of materials, tools and manpower to installing installing members of Goals with nets dimensions (4 x 2.1 m) use pipe dimeter 3 inch thickness 2mm and paint them with three layers from alraadlit,the work incude all accessoreis to have complete work.All needed work to complete the job will be included within the price. | no. | 1
246 | Benches for playground: Supply of materials, tools and manpower to installing benches for reserve players and coaches with dimensions of 3m x 0.5m x 0.5m, with a kirby canopy made, and the base made of plywood and painted white in three layers,the work incude all accessoreis to have complete work. All needed work to complete the job will be included within the price. | no. | 1
Total

## Mechanical Works
MECHANICAL WORKS
# | Item Description | Unit | Qty | Price $
1 | Supply manpower and equipment to dig Artesian well done by water well drilling excavator with a depth between(30-100m) , shall supply continuous water, work also includes: supply and installation of perforated metal pipes not less than 3 mm thickness with all connections and aggregate filter around the pipes, cleaning and disposal of excavated materials, monitoring water quality and underground layers if it contain salts and sulfate to be protected by non-perforated pipes, Concrete base around the well (2x2x0.25m) with steel cover and lock at the same level of surrounding soil, all works shall be according to Engineer's instructions, Note: activity will not start until the contractor obtain permit form General Authority for Groundwater \ any other authority | meter depth | 1
2 | Supply tools , materials and manpower to install submersible pump (Italian origin or equivelnt) with discharge (below)with necessary accessories to fix it to the well opening , work to include all pipes and connections, all works needed to complete the job is included in the price and works shall be done according to Engineer's instructions
2.1 | I hp | no. | 1
2.2 | 2 hp | no. | 1
2.3 | 3 hp | no. | 1
2.4 | 5 hp | no. | 1
2.5 | 7 hp | no. | 1
2.6 | 10 hp | no. | 1
2.7 | 15 hp | no. | 1
2.8 | 20 hp | no. | 1
2.9 | 25 hp | no. | 1
3 | Fuel Tank with Base: Supplying and installing carbon steel fuel tank, (4 mm thickness black steel) cylindrical shape capacity of 10,000L, with the following requirement: a) steel base made of iron angles 75*75*6mm., with anti rust paint and three layers of oil paint. b) gate valves, fuel filters, ventilation. c) G.I. pipes dia 20mm with fittings. d) level monitor (oil proof). e) Steel ladder using square iron pipe of 50*50*2mm. f) fuel-meter European made. The price shall includes fittings, necessary accessories and all needed works to complete the job. | no. | 1
4 | Water Pump (below hp): Supplying materials, tools and manpower to install, connect and commissioning water pump of capacity () hp (with suitable discharge and head), including all required water connections using PVC pipe, electrical connections using outdoor waterproof type socket switch, with providing galvanized protective metal frame cage to cover the pump & accessories and all other requirements to complete a good work.
a | 1 hp | no. | 1
b | 2 hp | no. | 1
c | 3 hp | no. | 1
d | 5 hp | no. | 1
Valves
5 | Gate Valve: The gate valve shall be solid wedge non-rising stem, manually operated which can be installed in either horizontal or vertical position of the piping system. The nominal pressure of the valve shall be NP16.
a | 100 mm | no. | 1
b | 150 mm | no. | 1
c | 200 mm | no. | 1
d | 250 mm | no. | 1
e | 300 mm | no. | 1
f | 400 mm | no. | 1
g | 600 mm | no. | 1
h | 800 mm | no. | 1
6 | Butterfly Valve: Suppling the tools, materials, and manpower to install butterfly valve, with manual gearbox, PN(16), the body of the valve from ductile iron GGG50, the shaft and the disc from stanless steel, epoxy coated, T-70. all works according to the direction of the supervisor engineer.
a | 400 mm | no. | 1
b | 600 mm | no. | 1
c | 800 mm | no. | 1
d | 900 mm | no. | 1
7 | Check Valve: The check valve shall be of (NP16) double door type, it shall be compact wafer design to fit between flanges. The check valve doors shall be springing loaded, normally closed by means of by one or more heavy duty stainless steel torsion springs. Flow from the pump shall cause the doors to open and upon pump shutdown. The torsion springs will shut the doors before reverse flow starts and at appoint of zero velocity for quick closer Seating shall be resilient and water tight. The sealing element shall be Buna-n molded to the body.
a | 200 mm | no. | 1
b | 250 mm | no. | 1
c | 300 mm | no. | 1
d | 400 mm | no. | 1
e | 600 mm | no. | 1
f | 800 mm | no. | 1
g | 900 mm | no. | 1
8 | Foot valve: Syppling the tools, materials, and manpower to install strainer(FOOT-VALVE), And the permeability space for the strainer is not less than 1/3 of the tube suction area, the body of the valve, disk, and gates from ductile iron GGG50, and the strainer is from galvanized iron 4mm or steel. all works according to the direction of the supervisor engineer.
a | 200 mm | no. | 1
b | 250 mm | no. | 1
c | 300 mm | no. | 1
d | 400 mm | no. | 1
e | 600 mm | no. | 1
f | 800 mm | no. | 1
g | 900 mm | no. | 1
9 | Lawn Mower: Supply and test the manual lawn mower for the mow the grass for the football stadium land. All needed work to complete the job will be included within the price. | no. | 1
10 | Car lawn mower: Supplying and test the lawn mower for the mow the grass for the football stadium land. the car lawn mowe size must appropriate to the size of the stadium size (at least 3 donm), Power source Petrol. All needed work to complete the job will be included within the price. | no. | 1
11 | Pumps: Suppling, tools, mechinary, and manpower to install and test set of a new horizontal pumps, douple section split case, with below sizes, from European origin(KSB, Flowserve, Sulzer, or equivalent), the selection of the pumps will after providing the cataloge and all specification of the pumps, and by corrdination with the supervisior committee and according to the below specification: the shaft, the impeller, and the shaft sleeve are stainless steel (14.122, 14.301, 14.021), the rings made from bronze(88.10.2), with gland paking, and with electricale motoer, IP55, 1450rpm, 400V, 50HZ, three phase, with soft starter (from ABB, Schneider, Siemens or equivalent), all electrical protections (internal contector, electroincale overload, phase failure, voltmeter, ammeter, indication lamps, sensitive devices for, dry running, heat increasing (for ball bearing and coils), and with all protection devices. The price also include the following: 1- dismantling and remove the old pumps, joints, valves, pipes, supports and straps, and demolishing, electrical panel boards, cables, cable trays, instrumentation, and storing in specified store by end user. 2- The concrete base works are included, Supply material and cast concrete(should get samples and be tested in goverment lab fc=25mpa with 2 layers of steel network 12mm @20 cm) for base. 3- The price includes all requirements to make the system works properly. all works according to the direction of the supervisor engineer.
11.1 | Split case, Q= 200 m³/hr , H= 50 m | no. | 1
11.2 | Split case, Q= 250 m³/hr , H= 50 m | no. | 1
11.3 | Split case, Q= 200 m³/hr , H= 60 m | no. | 1
11.4 | Split case, Q= 300 m³/hr , H= 60 m | no. | 1
11.5 | Split case, Q= 400 m³/hr , H= 60 m | no. | 1
11.6 | Split case, Q= 400 m³/hr , H= 100 m | no. | 1
11.7 | Split case, Q= 500 m³/hr , H= 40 m | no. | 1
11.8 | Split case, Q= 500 m³/hr , H= 60 m | no. | 1
11.9 | Split case, Q= 1000 m³/hr , H= 80 m | no. | 1
11.1 | Split case, Q= 1500 m³/hr , H= 40 m | no. | 1
11.11 | Split case, Q= 1500 m³/hr , H= 60 m | no. | 1
11.121 | Split case, Q= 2000 m³/hr , H= 60 m | no. | 1
11.13 | Split case, Q= 2000 m³/hr , H= 80 m | no. | 1
11.14 | End section, Q= 60 m³/hr , H= 40 m | no. | 1
11.15 | End section, Q= 60 m³/hr , H= 50 m | no. | 1
11.16 | End section, Q= 100 m³/hr , H=50 m | no. | 1
11.17 | Multi stage, Q= 400 m³/hr , H=100 m | no. | 1
11.18 | Multi stage, Q= 200 m³/hr , H=150 m | no. | 1
11.19 | Multi stage, Q= 250 m³/hr , H=200 m | no. | 1
11.2 | Multi stage, Q= 150 m³/hr , H=200 m | no. | 1
11.21 | Submersible pump, Q= 400 m³/hr , H=40 m | no. | 1
11.22 | Submersible pump, Q= 200 m³/hr , H=40 m | no. | 1
11.23 | Submersible pump, Q= 250 m³/hr , H=40 m | no. | 1
11.24 | Submersible pump, Q= 40 m³/hr , H=00 m | no. | 1
12 | Duct Works supply and installed Galvanized steel ducting - For air supply system including insulation density 24kg/m3 inside thickness 25mm,outside thickness 50mm and aluminum cladding , all beads, junctions, reducers, volume dampers, splitter damper and flexible joints as specified and as shown on drawings Coreference drawing No. ME-HVAC-DUCT -For return system including all beads, junctions, reducers, splitter damper and flexible joints as specified and as shown on drawings , Reference drawing No. ME-HVAC-DUCT - Supply & return wall grill grilles type SGR with VCD volume controal damper,duct flexible for supply insulation ,plenume box and HEPA filter. The work includes designing the ducts dimension according to the requirmnets, complete with all accessories and suppot. The work also includes leakage test after completing all work.
a | Supply air flow duct | m.l | 1
b | Return air flow duct | m.l | 1
c | Linnear L1 Size (12"X4") | no. | 1
d | Linnear L2 Size(20"X4") | no. | 1
e | Variable air volume VAV | no. | 1
13 | Elevator: Supply, installation , testing and commissioning of capacity (600 Kg), the building consist from 4 floors , (pit dimension 240cmX310cmX 120depth), (elevator shaft dimension 240cmX310cm), (machine room dimension" 240cmX310cmX195cm high), 1.0 m/s speed for operation on 415 V, 3 Phase, 50 Hz, variable frequency type traction control, electro magnetic brake system, simple operation, operating panel with luminous buttons, over load warning indicator, battery operated alarm bell, CFL type emergency light, intercom suitable for hook up to Society EPBAX, infrared rays sensing door protection for suitable height, reverse phase relay on controller, UPS system for emergency , digital car position indicator in car and at all positions indicator in car at all floors with UP/DOWN directions, light fixtures, ventilation fan etc. complete with all accessories including automatic rescue device and having following other features. As per attached technical specification and data sheet according to specification, All items should be implemented according to drawings and instructions of site engineer. | no. | 1
14 | Galvanized duct Supply and installation of different sizes of air ducts ,Supply air galvanized gauge 20 and specified to ASHRAE standards , installed connected and tested complete with joints, reinforcements, vanes, splitter dampers, access doors, elbows, reducers, fittings, hangers, supports using galvanized steel channels , the distance between supports is 1m, duct sealant and accessories . Duct insulation :Fiberglass blanket duct insulation for supply, fresh air and return ductwork, density 24 kg/m3, factory laminated to a reinforced foil Kraft vapor barrier facing covered, installed connected and tested complete including self adhesive fixing pins, sealing tape, wire banding with all the required works to complete the Job. | m.l | 1
Rehabilitation Water network
15 | Polyethylene Pipe Installation D mm,(D inch), PN10: Supply tools and materials to install, connect and test polyethylene pipe (10 bar) Suitable for Drinking water (D mm. dia.) (certificate of European (preferably Western) origin and/or Turkish origin or equivilant) according to Iraqi Specifications, complete with all needed fittings (elbows, tees, couplings, gaskets, reducers, welding pipes... etc.) and as specified below : Execution: the work Should be as following: - Using joints in conecte pipe to other. - Supply and Laying (10) cm clean garden sand under the Pipe, arrounding the pipe and 15 cm top of the pipe. - Installation and connections should be carried out using couplings (original quality), with all needed fittings. - Make hydrostatic pressure test for the Pipes according to specifications of General directorate of Water - Iraq , to ensure there is no leak in the Pipe Line . - Supply and fill fine soil around the pipes with minimum thickness 10cm. -Supply and laying warning tape, its specification(Width, Type, text on it, thickness, etc ) should be as per DOW specifications to be installed on the top of the first backfill compacted layer. - The Price Include all needed work to complete the job according to the Drawings, specification, and instruction of the Ta'afi and DoW Engineers.
a | D 75mm (3 inch) | m.l | 1
b | D 100mm (4 inch) | m.l | 1
c | D 150mm (6 inch) | m.l | 1
16 | Fittings: Supply and install all needed mentioned fittings such as (elbow, 45°, 90°, T connection, reducer, end cap, etc.) must be best quality. samples of key items will be requested and approved by supervisor Engineer before implementation.
a | Fitting T reducing (8 inch to 4 inch): supply and install T reducing 8 inch to 4 inch, 16 bar. | no. | 1
b | Fitting T reducing (4 inch to 3 inch): supply and install T reducing 4 inch to 3 inch, 10 bar. | no. | 1
c | Fitting T (4 inch to 4 inch): supply and install T reducing 4 inch to 4 inch, 10 bar. | no. | 1
d | Fitting (End Cap) plug: supply and install plug 4 inch, 10 bar. | no. | 1
e | Fitting (End Cap) plug: supply and install plug 3 inch, 10 bar. | no. | 1
f | Fitting Elbow 45 or 60 degree: supply and install Elbow 45 or 60 degree, 4 inch, 10 bar. | no. | 1
17 | Manhole Supply materials, tools and manpower to build manholes for iron valves with the specifications: - Interior dimensions (1*1) m, and depth 1m. - Casting reinforced concrete 1:2:3 (21 MPA), and for the steel bars use 12 mm for two layers with 15 cm c/c. - Cement plastering for inside and outside of walls. - Painting 3 layers of epoxy for inside and outside walls. - Casting reinforced concrete 25 mpa for the slab with use steel bars two layers @12 mm, 15 cm c/c. - Install stell cover (40*40) cm, in center of the manhole slab by use steel bars 1 inch with thickness 3 mm, and plate at least 5 mm. See attached drawing #37. | no. | 1
18 | Household Connections Supply materials, tools and manpower to connect households to the water network using 1/2" PPR pipe, including supply and connect good quality clamps (160 -110 -63mm) with PPR pipes 1/2" length not less than 80cm with closing the ends by caps with all necessary excavations and works needed to complete the work according to instructions of supervisor engineer. | m.l | 1
19 | Network hydraulic testing Hydraulic testing of network using air compressor for testing max pressure around 16 bar. Using Barometer gauge for measuring (best type). Tests conducted according to the BS6700 standard. | L.S | 1
Total

## Electrical Works
ELECTRICAL WORKS
# | Item Description | Unit | Qty | Price $
1 | Transformer 11/0.4KV capacity 400kVA Supply and install a good quality oil type hermetically sealed transformer (ATS, SEM or TEK) or equivalent brand, with the following specifications: 400kVA, 3-PHASE, Temp Rise 40/45°, Isolation A, Type Outdoor, Service Continue, Frequency 50Hz, with (Buchlose, Tap changer, relay). with two galvanized Electrical poles 11m Height ST 52 type, the foundation for transformer base concrete with diminutions (40cm,40cm,120cm) with concrete design mixing 4:2:1 cover all concert foundation with Asphalt Paint (flunkout) earthing system for both Neutral point and the frame of transformer using copper cable 1cx 50mm² with10m length, and two earth rods (1.5m) earth to be connecting from both sides of transformer with all necessary accessories clamps, glands, nuts and bolts. connect set link fuses with lighting arrester and all suspending accessories, supply and connect with each transformer Electrical Metal panel Board consist with two MCCB 250A with all connection accessories, board connect with low side of transformer throw copper cables 1cx 150mm². other side connect with overhead line through Aluminum –Copper clamps, the support for transformer set galvanizes bracket (210cm) L Channel type with 80cm U channel type with all accessories of installation, connecting H.T side of transformer with link fuss using ACC wire 50mm², and connect Cutout fuse side with 120/20 overhead lines using Aluminum –Aluminum clamps. All the electrical work will be completed under the instruction and supervision of the committee. All work should be according to the Iraqi technical specification for transformers D26. All the works will be directed by instruction of supervisor engineer. | no. | 1
2 | Transformer 11/0.4KV capacity 400kVA Supply without installation, with the same specs in item #1 in above. | no. | 1
3 | Transformer 11/0.4KV capacity 250kVA Supply and install a good quality oil type hermetically sealed transformer (ATS, SEM or TEK) or equivalent brand, with the following specifications: 250kVA, 3-PHASE, Temp Rise 40/45°, Isolation A, Type Outdoor, Service Continue, Frequency 50Hz, with (Buchlose, Tap changer, relay). with two galvanized Electrical poles 11m Height ST 52 type, the foundation for transformer base concrete with diminutions (40cm,40cm,120cm) with concrete design mixing 4:2:1 cover all concert foundation with Asphalt Paint (flunkout) earthing system for both Neutral point and the frame of transformer using copper cable 1cx 50mm² with10m length, and two earth rods (1.5m) earth to be connecting from both sides of transformer with all necessary accessories clamps, glands, nuts and bolts. connect set link fuses with lighting arrester and all suspending accessories, supply and connect with each transformer Electrical Metal panel Board consist with two MCCB 250A with all connection accessories, board connect with low side of transformer throw copper cables 1cx 150mm². other side connect with overhead line through Aluminum –Copper clamps, the support for transformer set galvanizes bracket (210cm) L Channel type with 80cm U channel type with all accessories of installation, connecting H.T side of transformer with link fuss using ACC wire 50mm², and connect Cutout fuse side with 120/20 overhead lines using Aluminum –Aluminum clamps. All the electrical work will be completed under the instruction and supervision of the committee. All work should be according to the Iraqi technical specification for transformers D26. All the works will be directed by instruction of supervisor engineer. | no. | 1
4 | Transformer 11/0.4KV capacity 250kVA Supply without installation, with the same specs in item #3 in above. | no. | 1
5 | Transformer 11/0.4KV capacity 100kVA Supply and install a good quality oil type hermetically sealed transformer (ATS, SEM or TEK) or equivalent brand, with the following specifications: 100kVA, 3-PHASE, Temp Rise 40/45°, Isolation A, Type Outdoor, Service Continue, Frequency 50Hz, with (Buchlose, Tap changer, relay). with two galvanized Electrical poles 11m Height ST 52 type, the foundation for transformer base concrete with diminutions (40cm,40cm,120cm) with concrete design mixing 4:2:1 cover all concert foundation with Asphalt Paint (flunkout) earthing system for both Neutral point and the frame of transformer using copper cable 1cx 50mm² with10m length, and two earth rods (1.5m) earth to be connecting from both sides of transformer with all necessary accessories clamps, glands, nuts and bolts. connect set link fuses with lighting arrester and all suspending accessories, supply and connect with each transformer Electrical Metal panel Board consist with two MCCB 250A with all connection accessories, board connect with low side of transformer throw copper cables 1cx 150mm². other side connect with overhead line through Aluminum –Copper clamps, the support for transformer set galvanizes bracket (210cm) L Channel type with 80cm U channel type with all accessories of installation, connecting H.T side of transformer with link fuss using ACC wire 50mm², and connect Cutout fuse side with 120/20 overhead lines using Aluminum –Aluminum clamps. All the electrical work will be completed under the instruction and supervision of the committee. All work should be according to the Iraqi technical specification for transformers D26. All the works will be directed by instruction of supervisor engineer. | no. | 1
6 | Transformer 11/0.4KV capacity 100kVA Supply without installation, with the same specs in item #5 in above. | no. | 1
7 | HT galvanized Electrical Tubular 11m: Supply Install test H.T galvanized Electrical tubular poles 11m Height ST 52 type with thickence 5.5mm, the work including excavation for pole foundation (50cm *50cm*180cm ) concreting foundation dimension form work concert (40cm ,40cm ,210cm) with concrete design mixing 4:2:1 cover all concert foundation with Asphalt Paint (flunkout), and to be backfill space between pole foundation and excavated area with a suitable backfill soil with very good compaction, all the works will be directed by instruction of supervisior engineer. | no. | 1
8 | HT galvanized Electrical Tubular 11m: Supply without installation, with the same specs in item #7 in above. | no. | 1
9 | HT galvanized Electrical Lattice 11m: Supply, Install and test H.T galvanized Electrical lattice poles 11m Height ST- 52 type work including excavation pole foundation (50cm *50cm*180cm ) concreting foundation dimension form work concert (40cm ,40cm ,210cm) with concrete design mixing 4:2:1 cover all concert foundation with Asphalt Paint (flunkout) backfill space between bole foundation and excavated area with a suitable backfill soil with very good compaction and making the alignment for the pole, and the connection with all necessary accessories, clamps, glands ,nuts bolts and washer. all the works will be directed by instruction of supervisior engineer. | no. | 1
10 | HT galvanized Electrical Lattice 11m: Supply without installation, with the same specs in item #9 in above. | no. | 1
11 | LT galvanized Electrical Tubular 9m: Supply Install test LT galvanized Electrical tubular poles 9m Height ST 52 type with thickence 5.5mm, the work including excavation for pole foundation (50cm *50cm*180cm ) concreting foundation dimension form work concert (40cm ,40cm ,210cm) with concrete design mixing 4:2:1 cover all concert foundation with Asphalt Paint (flunkout), and to be backfill space between pole foundation and excavated area with a suitable backfill soil with very good compaction, all the works will be directed by instruction of supervisior engineer. | no. | 1
12 | LT galvanized Electrical Tubular 9m: Supply without installation, with the same specs in item #11 in above. | no. | 1
13 | LT galvanized Electrical Lattice 9 m Height Supply ,Install, and test LT galvanized Electrical Lattice 9 m Height ST 52 type work including excavation pole foundation (50cm *50cm*150cm ) concreting foundation diminutions formwork concert (40cm ,40cm ,180cm) with concrete design mixing 4:2:1 cover all concert foundation with Asphalt Paint (flunkout) connect earthing using copper cable 1cx 50mm2 with 1.5m length to be connected with earth rods (1,5m) with all accessories Copper clamps, glands, nuts and bolt , backfill space between bole foundation and excavated area with a suitable backfill soil with very good compaction , and making the alignment for the pole . all the electrical works will be completed under instruction and supervision of the committee.See Annex (6) for Lattice poles 9m ST- 52 | no. | 1
14 | LT galvanized Electrical Lattice 9 m Height Supply without installation, with the same specs in item #13 in above. | no. | 1
15 | Supply, install and test 120cm galvanized Channel bracket with clamps, glands, nuts and bolt , and all necessary connection and accessories needed. all the works will be directed by instruction of supervisior engineer. | no. | 1
16 | Channel bracket (Supply without installation, with the same specs in item #15 in above). | no. | 1
17 | Supply, install and test Pin Insulator 11KV with Spindle, and all necessary connection and accessories needed, all the works will be directed by instruction of supervisior engineer. | no. | 1
18 | Pin Insulator 11KV with Spindle (Supply without installation, with the same specs in item #17 in above). | no. | 1
19 | Supply Disc Insulator 11KV with complete accessories According to specifications, all the works will be directed by instruction of supervisior engineer. | no. | 1
20 | Disc Insulator 11KV (Supply without installation, with the same specs in item #19 in above). | no. | 1
21 | Supply, test and installation ACSR Wire (Aluminum) 120mm² and according specifications. All the works will be directed by instruction of supervisior engineer. | m.l | 1
22 | ACSR Wire (Aluminum) 120mm² (Supply without installation, with the same specs in item #21 in above). | m.l | 1
23 | Supply, test and installation ACSR Wire (Aluminum) 95mm² and according specifications. All the works will be directed by instruction of supervisior engineer. | m.l | 1
24 | ACSR Wire (Aluminum) 95mm² (Supply without installation, with the same specs in item #23 in above). | m.l | 1
25 | Supply, test and installation ACSR Wire (Aluminum) 50mm² and according specifications. All the works will be directed by instruction of supervisior engineer. | m.l | 1
26 | ACSR Wire (Aluminum) 50mm² (Supply without installation, with the same specs in item #25 in above). | m.l | 1
27 | Supply, test and installation stay rod, and according the specifications. All the works will be directed by instruction of supervisior engineer. | no. | 1
28 | Stay rod (Supply without installation, with the same specs in item #27 in above). | no. | 1
29 | connect Aluminum -Aluminium clamps (multi size) Supply, test, connect Aluminum -Aluminium clamps. All work must be implemented according to the instructions of the supervising engineer. | no. | 1
30 | connect Aluminum -Aluminium clamps (multi size) (Supply without installation, with the same specs in item #25 in above). | no. | 1
31 | connect insulator with clamps and screws Supply, test , connect insulator with clamps and screws .All work must be implemented according to the instructions of the supervising engineer. | no. | 1
Lighting work
32 | Lighting Poles H 15m: Supplying, erecting Galvanizing Lighting poles 15m height (tower type with step arrangement to climb for repair & maintenance) with circular cage on pole top for projectors fixture (6 No. of 400 W water proof type projector with 6* photo cell 5A) and connect wire 1.0KV (4*4mm²) PVC insulated copper cable for set (6projectors) from source point inside HDPE /Pe pipe within Excavation 40cm and backfilling it, and earthing the pole with wire (1*2.5mm²) and cu rod 1m*16mm² separately or with another poles connect together by one earthing grid, Price includes supplying, erecting, excavating/digging and making concrete for pole base with nut and bolts arrangement to complete works as required. | no. | 1
33 | Park and Garden LED lighting poles (decorative lighting poles): Supply, install, connect and commission of Park and Garden LED lighting poles, (the length according to the light power, 3-6m) includes casting concrete base of erect poles and base plate with fixing it by (4) anchor bolts for each pole with all accessories, The price includes supplying, installing, connecting, testing and commissioning with necessary accessories,
a | 50W | no. | 1
b | 80W | no. | 1
c | 100W | no. | 1
d | 150w | no. | 1
34 | Projector LED Light : Supplying, Installing, connection ,and commission of LED light projector 230V, with drives (not less than IP66 ) and connecting wire 2*2.5mm² 1.0kv with 5A photo cells for each projector in side PVC pipe with switches and junctions fixed with wall ,connect with existing source points and all accessories,The price includes supplying, installing, connecting, laying and commissioning drilling, cutting to complete works as required.
a | 800 w | no. | 1
b | 400 w | no. | 1
c | 200 w | no. | 1
d | 150 w | no. | 1
e | 100 w | no. | 1
f | 80 w | no. | 1
g | 50 w | no. | 1
35 | LED Lighting (outdoor) 24w: Supplying ,Installation, testing and commissioning of prewired outdoor fittings of all pendant type complete set, includes wiring/connecting with 1.0 kV grade 2*1.5mm² PVC insulated copper cable/wires laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (20 mm dia) with 6 A switches with all accessories. The price includes supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
36 | LED Lighting (indoor) 24w: Supplying ,Installation, testing and commissioning of prewired indoor fittings of all pendant type complete set, includes wiring/connecting with 1.0 kV grade 2*1.5mm² PVC insulated copper cable/wires laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (20 mm dia) with 6 A switches with all accessories. The price includes supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
37 | Bracket Lighting [ old wiring ] Supply, install, connect and commissioning to replace and install a new Lighting Fixture using the old existing wiring, and the old existing switch with all the required works to complete the Job. | no. | 1
38 | Ceiling Lighting: Supplying ,Installation, testing and commissioning of prewired ceiling LED fittings of all pendant type complete set, includes wiring/connecting with 1.0 kV grade 2*1.5mm² PVC insulated copper cable/wires laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (20 mm dia) with 6 A switches with all accessories. The price includes supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
a | 10 w | no. | 1
b | 15w | no. | 1
c | 18w | no. | 1
d | 24w | no. | 1
e | 36w | no. | 1
f | 48 w | no. | 1
39 | LED 48W Lighting fixture: Supplying and connecting LED Lighting Panel 48W/220VAC( 60cmx 60cm) Ultra Bright LED aluminum base with 1.0 kV grade 2*1.5mm² PVC insulated copper cable/wires laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (20 mm dia) with 6 A switches with all accessories. The price includes supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
40 | Street lighting Poles: Supplying, erecting, testing Galvanizing Lighting poles the height as below. Price includes supplying, erecting, excavating/digging and making concrete for pole base with nut and bolts arrangement to complete works as required. The street lighting poles shall be manufactured from steel sheets and having the following features. 7, 10-meter height galvanized steel shaft octagonal cross section and tapered from bottom to top, and made of one piece. 12, 15-meter height galvanized steel shaft with octagonal cross section and tapered from bottom to top, and made from two pieces joined together by slip joint method, the slip joint overlap must be at least 1.5 times the largest inside diameter of the female section. For all types, the thickness of the shaft wall will be 4mm minimum. All works according to the Iraqi technical specification of street lighting poles-D13. All the works will be directed by instruction of supervisior engineer.
a | 7m single arm | no. | 1
b | 7m double arm | no. | 1
c | 10m single arm | no. | 1
d | 10m double arm | no. | 1
e | 12m single arm | no. | 1
f | 12m double arm | no. | 1
g | 12m triple arm | no. | 1
h | 15m single arm | no. | 1
j | 15m double arm | no. | 1
k | 15m triple arm | no. | 1
41 | LED Streetlight (below power) W: Supply a high quality LED (as below W) outdoor streets light, pure white 4000-6500k, working temprature(-20 to 50 C˚), working life hours (100,000 hr), protection level(IP67), body color (dark grey), warranty (2 year),Lm(15000-16500lm), Voltage (V): AC 85 - 265 V, 50/60HZ, body material (aluminum), Each street light should be controlled by a high quality 5A photo cell, photo cell should be fixed on the body of the street light in a way to keep it IP67,All connection and installation accessories with all the required works to complete the Job."
a | 80 watt /80 watt ( with installation/witout installation) | no. | 1
b | 100 watt ( with installation/witout installation) | no. | 1
c | 150 watt ( with installation/witout installation) | no. | 1
d | 200 watt ( with installation/witout installation) | no. | 1
e | 250 watt ( with installation/witout installation) | no. | 1
42 | Control Board: Supply, installation, testing of control board (timing switch-photocell) out door type fabricated with 2mm thick sheet steel with all complete connections required for lighting opreation control supply as per required specifications. All the works will be directed by instruction of supervisior engineer. | no. | 1
43 | Street Luminaires and Floodlights 400W: Supply a high quality Street Luminaires and Floodlights 400W outdoor street light,protection level (IP65),Lm (48000lm),pure white polymer Inj.Body-Aluminium Reflector-Tempered Glass,Each street light should be controlled by a high quality 10A photo cell, photo cell should be fixed on the body of the street light in a way to keep it IP65,All connection and installation accessories with all the required works to complete the Job." | no. | 1
44 | Lighting lanterns: Supply, install, connect and commission of Lighting lanterns on the external fence columns with LED lamp of 50 watts using a (2*2.5) mm² cable. All work must be implemented according to the instructions of the supervising engineer. | no. | 1
45 | Park and Garden Solar LED lighting poles 60w: Supply, install, connect and commission of Park and Garden Solar LED lighting poles 60w, with solar panel, battery, and LED light, (ALL in ONE TYPE) and with pole, the poles hight about 4m, dia. 8 cm and thickness 3 mm, includes casting concrete base of erect poles and base plate with fixing it by (4) anchor bolts for each pole with all accessories, The price includes supplying, installing, connecting, testing and commissioning with necessary accessories, | no. | 1
46 | Colorful lights points : Supply and install lights with deferent colors (40 watts each, with wires 3x2.5mm²) the power cable should be (3x6mm²), the lights point should be installed on the spcific places, the price include all plastic pipes (3cm diameter for cables, any steel base needed), all according to supervisor engineer. | no. | 1
47 | Bracket waterproof wall fixture: Supplying & Installing of bracket waterproof wall prewired outdoor lighting luminaries fixture suitable for GLS lamp 230VAC/23 watts complete with all accessories such as base, LED drive & LED bulb, glass, reflector, louvered includes connecting with one way 6 Amps switch and wiring with 1.0KV grade 2 x 1.5 mm² PVC insulated copper wires with all accessories. The price includes supplying,installing,connecting,laying and commissioning to complete works as required. | no. | 1
48 | External Lighting: Supplying, Installation, testing and commissioning of prewired LED water proof fittings of all pendant type complete set with 360W includes wiring/connecting with 1.0 kV grade 2*1.5mm² PVC insulated copper cable/wires if required, with 6 A switches with all accessories. The price includes supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. All needed works to complete the job, shall be included within the price. | no. | 1
Cable works
49 | HT 11KV Power Cable: Supplying, Installing, Laying , test and Connection of power Cable (12/20KV) XLPE 3*150mm², 11kV heat shrink joints, armored type from the source to transformers. The price includes supplying, installing, laying{if under ground shall be inside (100*40cm) excavation and backfilling by soft stand, warning type and concrete Block} the connection include ended cable joints(4 set), with all necessary requirements to complete work as required. All the works will be directed by instruction of supervisior engineer. | m.l | 1
50 | LV Power Cable: Supply, install, test and lay 1.0 kV grade PVC insulated sheath-un-Armored copper cable. laid in side PVC pipe and existing concrete manholes, The price includes supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning include (cable termination with Cu lugs at both end) to complete works as required.
a | 1x240 mm² | m.l | 1
b | 1x150 mm² | m.l | 1
c | 3x95+1x50 mm² | m.l | 1
d | 4x75 mm² | m.l | 1
e | 4x50 mm² | m.l | 1
f | 4x35 mm² | m.l | 1
g | 4x16 mm² | m.l | 1
h | 4x10 mm² | m.l | 1
j | 2x10 mm² | m.l | 1
k | 2x6 mm² | m.l | 1
l | 4x6 mm² | m.l | 1
m | 4x4 mm² | m.l | 1
n | 2x4 mm² | m.l | 1
o | 2x2.5 mm² | m.l | 1
p | 2x1.5 mm² | m.l | 1
q | 1x1.5 mm² | m.l | 1
51 | LV Power Cable: Supply, install, test and lay 600/1000V Low Voltage Twisted Aluminum Cable. The price includes supplying, installing, connecting, laying, include (cable termination with clamp) to complete works as required.
a | 1x16 mm² | m.l | 1
b | 1x35 mm² | m.l | 1
c | 1x50 mm² | m.l | 1
d | 1x70 mm² | m.l | 1
e | 1x95 mm² | m.l | 1
f | 3x95+1x70 mm² | m.l | 1
52 | Cable Trench & laying cable: Supplying materials, tools, equipment and manpower for ground excavation for cable trench (W=50cm x70cm).Including, surface cutting, drilling, excavation, backfill first clean sand layer 10cm, laying cables, second clean sand layer 10cm, new concrete tiles, sub base material layer, warning tape, re backfill & restore the ground. The price include laying cables, installing cable markers(in distances not les than 20m and ground restoration either concrete, asphalt, to complete the work as required. | m.l | 1
53 | Galvanized Steel Perforated Cable Trench with cover and laying old cables: Supplying materials, tools, equipment and manpower for installation Galvanized Perforated steel Cable Trench for cable trench (10cm x5 cm X thickness 3mm)for laying old cables In coordination with the local electricity department, the work includes repairing and compensating for any shortfall in cables that occur as a result of diverting them into the trench.Including, surface cutting, drilling in wall and ceiling for laying old cables with repair the damage in plastering that caused on work. All needed works to complete the job will be included within the price. | m.l | 1
Electrical switches work
54 | Socket Switch(13A): Supplying & fixing of combine 13A, 5 pin universal switch-socket with shuttered & indicator outlet, on PVC molded tough surface box includes wiring/connecting with 1.0 kV grade 3*2.5mm² PVC insulated copper cable/wires laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (20 mm dia) with all accessories. The price includes supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required) and commissioning to complete works as required. | no. | 1
55 | Outlet Socket (13 Amp) [ old wiring ] Supply, connect and operate just outlet switched socket 13 Amp 2P+E, by using the old existed wiring | no. | 1
56 | Universal Socket Switch 15A: Supplying & fixing of combine 15A, 5 pin universal switch-socket with shuttered & indicator outlet, on PVC molded tough surface box includes wiring/connecting with 1.0 kV grade 3*2.5mm² PVC insulated copper cable/wires laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (20 mm dia) with all accessories. The price includes supplying,installing,connecting,laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
57 | Light Switch: Supply, install, connect and commission (230VAC/6A) (single, double, triple and quadruple) light switches includes wiring with 1.0 kV grade 2*1.5mm² PVC insulated copper cable/wires laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (20 mm dia) with all accessories. The price include supplying, installing, connecting, laying, drilling & cutting (concrete wall if required ) and commissioning to complete works as required. | no. | 1
Fan works
58 | Industrial Exhaust fans: Supplying, Installing, Test and commission of Industrial exhaust Fan (60*60cm ),with 3ph motor/380- 415 v, 220 W, 1400 rpm, 7400 m³per hrs. includes wiring with 1.0 kV grade 4*2.5mm² PVC insulated copper cable laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (20 mm dia) with all accessories. The price includes supplying, Installing, connection , testing, drilling & cutting ( concrete wall if required on existing place ) to complete work as required. for motors hall. | no. | 1
59 | Exhaust fan: Supplying, Installation, testing and commissioning of exhaust fan with Aluminum louvers 220 volt A.C 1400 rpm with all accessories such as frame with arm 3 Nos. sweep 3 Nos., condenser and fan body etc., price includes connecting SP 1-way 6A switch with 1.0 kV grade 2x1.5 mm² single core PVC insulated copper wire, passing through surface PVC conduit pipe, The price includes supplying, installing, connecting, laying and commissioning drilling, cutting to complete works as required.
a | 6'' | no. | 1
b | 8'' | no. | 1
c | 10'' | no. | 1
d | 12'' | no. | 1
e | 16'' | no. | 1
f | 20'' | no. | 1
60 | Ceiling fan: Supplying, installing, test and commission of ceiling fan (240 volt A.C 1400 rpm,1400mm sweep with 56"), down rod of standard length unto 300mm with accessories such as down rod, sweep 3 Nos., canopy 2 Nos., condenser, fan body and fan regulator includes wiring with (2x1.5mm²) 1.0kV grade , PVC insulated copper cable/wires laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (20 mm dia) wherever not possible with all accessories. The price includes supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
61 | False Ceiling Fan: Supply, install, test and commission electrical ceiling fan size 60x60 cm specially for false ceiling with remote multi speeds control and using 1.0 kV grade, 2x1.5mm² PVC insulated copper cable/wires laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (20 mm dia) with all accessories. The price includes supplying,installing,connecting,laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
62 | Wall fan: Supplying, installing, test and commission of wall fan (240 volt A.C 1400 rpm,1400mm), with (2x1.5mm²) 1.0kV grade , PVC insulated copper cable/wires laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (20 mm dia) wherever not possible with all accessories. The price includes supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
Board Work
63 | Distribution Boards (repair): Supplying tools, matirals and manpower to maintenance of MDB, the work shall include replacing any defected MCB, MCCB, Clock timers, and indication lamps, the work also shall include additional 3phase 40A MCB, and 3 numbers single phase 16A MCB. | ls | 1
64 | Distribution Boards (new): Supplying tools, matirals and manpower to install of MDB, the work shall include (no.) MCB, MCCB, Clock timers, and indication lamps, the work also shall include additional 3phase 40A MCB, and 3 numbers single phase. | no. | 1
65 | Main Distribution Board (3ph MDB): Supply, install and connect Main distribution board with metal stand consist of metal board box of (140cm x 100cmx 60cm) with IP66 outdoor boards, digital screens of Ammeter, voltage and frequency meters, signal lamps, bus bar, with all connection and installations items with all accessories. The Price includes supply, install, connect, and commission, necessary cutting, drilling, testing with all accessories to complete works as required. A- [(1No.)3 ph., kilowatt hour (kWh)meter, 400V, 200 A] B- [(1 No.) 400A, 3 Pole. MCCB type, breaking capacity 25KA, 415 volt A.C]. C- [(2 No.) 150A, 3Ph. MCCB type, breaking capacity 25KA, 415 volt A.C]. D- [(2 No.) 100A, 3Ph. MCCB type, breaking capacity 16KA, 415 volt A.C]. E- fire extinguisher. F- (4 strips) Copper Bus-Bar 80 cm length 500A, (for three phase lines and neutral) with separate earth strip, G- (2 No) Residual current circuit breaker (RCCB), with a leakage sensitivity not exceeding 0.03 amp. | no. | 1
66 | Main Distribution Board (1ph MDB): Supply, install and connect Main distribution board with metal stand consist of metal board box of (60*80) cm dimension(wither proof type), digital screens of Ammeter, voltage and frequency meters, signal lamps, bus bar of 100 Amp capacity for each one, with all connection and installations items with all accessories. The Price includes supply, install, connect and commission, necessary cutting, drilling, testing with all accessories to complete works as required. A - [1No.)1 ph, kilowatt hour (kWh)meter, 220V, 200 A] B- [(1No.) 1x100A, MCCB type]. C- [(10 No.) 2x10 A, MCB Type] D- fire extinguisher. E- (2 No) Residual current circuit breaker (RCCB), with a leakage sensitivity not exceeding 0.03 amp | no. | 1
67 | Sub Distribution Boards( as below ways): Supplying, installing, testing and commissioning of for () ways, TPN DB (DIN type, horizontal/vertical) with single door complete set to accommodate incoming miniature circuit breaker (MCB) triple pole, (matched with board ways size) Amps, 415 volt A.C 16 kA, and outgoing SP MCB () x 32 Amps on/in prefabricated MS surface /MS cubical control panel board with separate neutral strip and all accessories.The price includes supplying,installing,connecting,laying, drilling, cutting and commissioning to complete works as required.
a | 6 ways | no. | 1
b | 12 ways | no. | 1
c | 18 ways | no. | 1
d | 24 ways | no. | 1
68 | Maintenance of Sub Distribution Board: Perform rearranging and replacing the door of exist distribution boards(vertical or horizontal) and if required (damaged wires, MCB..etc) with all accessories. The price include supplying, replacing missing parts/items, installing ,laying, connecting, drilling, cutting, painting, fixing with all accessories to complete as required. | no. | 1
69 | Earthing Systems: Supply, install and connect earthing system containing (according to attached earthing drawing ) ( with 3 number of 20 mm dia 1.5m length Copper rods each ( triangle or straight formation based on space availability) connect (with copper nut and bolts) each other at the surface with 1x50 mm² bare Cu conductor and to M.D.B and to SMDBs with 1.0 kV grade 1x 50 mm²from MBD inside the building,conncet by 1*16mm² with all socket and split unit with all accessories. Price includes supplying of all necessary materials /accessories (mixture of coal, salt and fine sand etc.), installing, laying, testing, commissioning, excavation pit LxW, 1.8 m x 0.5m ( for each cu rod and refill with mixture of coal, salt and fine sand etc.) to complete work as required . (Consider 3 pits = 1 set, where each pit consist of all materials/accessories as depicted in attached earthling drawing) | Set | 1
70 | Earthing System: Supply, install, test and commission a complete earthing system for the project including -but not limited to- all conductors, copper bars, clamps, conduits, earth,earth pits reference bars, test links, earth wires/cables, concrete inspection pits and its heavy duty steel or concrete cover, pull ropes and all civil work needed, all as per specifications and drawings, to achieve resistance not more than 1 ohm. | no. | 1
71 | Electric bell: Supplying and replacing of electrical call bell 1 ph/5W includes rewiring/connecting with 1.0 kV grade 2*1.5mm² PVC insulated copper cable/wires laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (20 mm dia) with 6 A door bell switch with all accessories. The price includes supplying,replacing,connecting,laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
72 | Wireless Fire alarm control panel: consist of 4 zones, with UPS and batteries to work during shutdawn the electrcity power, with covering all detectors & consists of the latest dual flash-based microprocessor technology combined with a high resolution, high contrast, graphical LCD display and tactile keypad providing a simple select and click programming aid for engineer configuration and end-user operation.
a | Intelligent wireless Smoke Detector. | no. | 1
b | Intelligent Addressable call point. | no. | 1
c | Addressable Fire alarm bell (siren). | no. | 1
d | Addressable lighting indicator. | no. | 1
73 | Fire alarm control panel: supplying tools, materials, and manpower to install of fire alarm system consist of 2 zones, from English brand or equivalent, with UPS and batteries to work during shutdown the electricity power, with covering all detectors & consists of the latest dual flash-based microprocessor technology combined with a high resolution, high contrast, graphical LCD display and tactile keypad providing a simple select and click programming aid for engineer configuration and end-user operation. the system sholud also include the items in belo: | no. | 1
a | Conventional heat Detector, with 1.0mm² heat resistant wire, with insulated and resistant heat pipes. | m.l | 1
b | Fire alarm bell (siren) and lighting indicator, with 1.0mm² heat resistant wire, with insulted and resistant heat pipes. | no. | 1
c | Conventional call point, with 1.0mm² heat resistant wire, with insulted and resistant heat pipes. | no. | 1
AC units
74 | AC units Supply, install, fixing, connect, test and commissioning wall mounted Split unit air-conditioning (Cool & Heat). The price include supply & installation of cable 3*4mm² also switch 45 A for single phase AC units and 4X6mm² with 3MCB 32 Amp for 3 phase AC units . Also the price include installation of the out door units on the roof of building or installed suspended with wall by special iron base with all accessories of the building with base vibration absorber height more than 4cm for out door units, protection cage, the devices also include all accessories with all extra copper pipes connections through the 3 inch PVC sleeve pipe also extra refrigerant gas, cable tray, the net work condensing 1 inch PVC pipe an must be connected to the nearest floor drain. With all accessories needed, as well as all needed works to complete the job entirely.
a | 48000BTUH Cassette type | no. | 1
b | 72000BTUH concealed duct type | no. | 1
c | 48000BTUH concealed duct type | no. | 1
d | 24000BTUH wall mounted | no. | 1
e | 48000BTUH vertical type | no. | 1
75 | Split Unit Air-Conditioning : Supply, install, connect and commission wall mounted Split unit Air-conditioning inverter type (Cool & Heat) (V)ton, Technical specification and Type of compressor T3, Type of refri. gas( R410a) includes wiring/connecting with 1.0 kV grade 3*4mm² PVC isolated copper cable/wires laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (20 mm dia) with 25 A switches with all accessories. The price includes supplying, installing, connecting, laying, drilling & cutting, and commissioning to complete works as required. All needed work to complete the job will be included within the price.
a | 1 Ton 12000BTUH | no. | 1
b | 1.5 Ton 18000BTUH | no. | 1
c | 2 Ton 24000BTUH | no. | 1
76 | Split Unit Air-Conditioning: Supply, install, fixing, connect, test and commissioning vertical type Split unit air-conditioning (Cool & Heat). The price include supply & installation of cable 3*4mm² also switch 45 A for single phase AC units and 4X6mm² with 3MCB 32 Amp for 3 phase AC units. Also the price include installation of the outdoor units on the roof of building or installed suspended with wall by special iron base with all accessories of the building with base vibration absorber height more than 4cm for outdoor units, protection cage, the devices also include all accessories with all extra copper pipes connections through the 3 inch PVC sleeve pipe also extra refrigerant gas, cable tray, the network condensing 1 inch PVC pipe an must be connected to the nearest floor drain. With all accessories needed, as well as all needed works to complete the job entirely.
a | 3 Ton 1ph. | no. | 1
b | 3 Ton 3ph. | no. | 1
c | 4 Ton 3ph. | no. | 1
62 | Air curtain Supply and install air curtain length 2.2m , air capacity 1650 m³/hr., silent operation, high efficiency, with all accessories required. | no. | 1
77 | Maintenance Maintenance, replacing, Testing, cleaning and operating of air conditioning split units off all types ( vertical, window , celling , wall mounted ), And the completion of the shortage in case of any defect appears during the operation, providing remote control or wired thermostat control for Each unit in case of loss or damage each according to capacity and type of air conditioning unit, And the obligation to connect all electrical connections required for operation, the price include all accessories works, insulation of supply and return pipes, connection the condensing pipes. | no. | 1
78 | Repair & Maintenance of Exist AC Units: Perform general inspection, maintenance and repair on the exist AC window mounted units & AC wall mounted split units of different sizes. The scope include repair, replace old damage parts, cleaning and washing both parts of the split units and refilling them with suitable gas. The price of works include supplying (including grid switch 25A,3MCB 32A & wires, moving units, if required) installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. | no. | 1
79 | SDB cover Supply and fixing (the cover only ) for an old sub distribution board , which is already exist in the site , the cover dimensions must be perfectly fit for the old SDB ,( the old SDB is of different brands and types ,so each cover may be different from the other , but it is approximately about 22 x 35 cm ) the work to be done according to the engineer instructions , with all required works to complete the job . | no. | 1
80 | Metallic Enclosure: supply and fixing metallic enclosure ( 40 x 50 x 25 ) cm with transparent plastic interface and with two signal lamp, the work include dismantling the existed main circuit breaker and KWH meter and re-install them in a systematic way using wooden board under them , with all required works to complete the job. | no. | 1
81 | 1ph circuit breaker supply and install single phase miniture circuit breaker (16 , 25 ,32, 40, 50, 63A) type C characteristic curve, thermal magnetic protection ( 6kA breaking capacity ) south korean or Turkish made ( or equvelent ), the work to be done according to the engineer instructions , with all required works to complete the job . | no. | 1
82 | JUNCTION BOX supply and install with the dimensions of 8 x 8 cm water proof plastic junction box (Universal type) with not less than IP 67/68 type and standard color coated ( for electrical connection inside it) include waterproof enclosure (with watertight gasket) to complete work as required. | no. | 1
83 | Lights With Motion Sensors Supplying ,Installation, testing and commissioning of prewired 40 Watt LED light with motion sensor builtin of all pendant type complete set, includes wiring/connecting with 1.0 kV grade 2*1.5mm² PVC insulated copper cable/wires laid inside existing concealed metal pipe and if required laid through new surface metal pipe (20 mm dia) with all accessories. The price includes supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required. The price include all necessary cable tray fixed to ceiling. The price also include removing old electric pipes, wiring and lights if necessary. All needed works to complete the job should be included within the cost. All work must be done according to the supervising engineer's instructions. | no. | 1
84 | Tree Lighting Supplying ,Installation, testing and commissioning of 20W Low Voltage Ground LED Spotlight Waterproof Outdoor Fixture (Water Proof (IP66). The price includes wiring/connecting with 1.0 kV grade 2*1.5mm² PVC insulated copper cable/wires if required with all accessories. The price includes supplying, installing, connecting, laying, drilling & cutting ( concrete wall if required ) and commissioning to complete works as required.the work include fixing LED spotlight on base according to the supervising engineer's instructions. All needed works to complete the job, shall be included within the price." | no. | 1
85 | Automatic lightning system: Supply, install, connect and commission of Photo Cell box waterproof enclosure metal frame made of iron sheets include (1 No) Residual current circuit breaker (RCCB), with a leakage sensitivity not exceeding 0.03 amp, and (1 No) Selector switch three options (On, Off and Auto) and (1x40A, 1PH,2Pole, magnetic contactor). The price includes supplying, installing, connecting, testing and commissioning with necessary accessories, dismantling all the existing damaged equipment / debris and dispose to the designated place to complete works as required. | L.S | 1
86 | Uninterruptible Power Supply (UPS) 10 KVA: Supply, install, connect, and test of UPS with 10KVA power, The UPS system will be floor mounted type. with eff. more than 90%, the price included the battries, and the UPS having 20 minutes back up along with rack for batteries. The UPS will conform to the Attached Technical Specifications. On the date of installation, the batteries should not be more than six months older from the date of manufacturing otherwise the same shall be rejected. The UPS alongwith batteries will be run for 20 minutes on full load to check the adequacy of capacity of batteries before accepting the work. | no. | 1
87 | Solar System: Supply of materials, tools and manpower to install a solar power system with below power capacity ()kw power, with the below items, and also adding the protections, boards, and/or any other required item to complete the job.the work also include training 2 employee for the maintenance works. SEE The Attached Specs.
a | Solar Inverter Hybrid
a1 | 3 kw | no. | 1
a2 | 5 kw | no. | 1
a3 | 6 kw | no. | 1
a4 | 7.5 kw | no. | 1
a5 | 10 kw | no. | 1
b | Solar Panel: Supply and provide new Solar Panels, with following specifications: Mono type, Bifacial, Half-Cut cell-12 Busbar/ or equivlent.
b1 | 350 watt | no. | 1
b2 | 450 watt | no. | 1
b3 | 550 watt | no. | 1
b4 | 660 watt | no. | 1
c | Batteries:
c1 | Supply and provide new Batteries Type PO4 Lithium, 280A, 48V, DoD 6000c@ 80% | no. | 1
c2 | Supply and provide new Batteries Type PO4 Lithium, 200A, 25V, DoD 6000c@ 80% | no. | 1
d | Cabels and Accessories: Suppy and and install all required AC and Dc cables, fuses and boxes, 3ph CB, MC4, and all that required to complete the work. | L.S | 1
e | Solar Array Structure: Supply and install new Solar Array Structure made of steel, standard shape and specifications: - Structure for Base: Hot dip galvanized and steel section L 40*40*3 mm - Structure for Leg: Hot dip galvanized and steel section tupe rectangulare 50*25*3 mm - Stand to be fixed above concrete base OR ground screw. All needed work to complete the job will be included within the price. | no. | 1
88 | FireFighting System Water System Supply, install, connect and commission water firefighting system with following details. The price include all material, accessories and work necessary to complete the work and have fully functional system.
a | Firefighting Pump Type (Electric + Diesel + Jockey) 450 G/min + Electric Board | no. | 1
b | Equiping Installing and operating booster system to fill the tanks with a capacity of 6 HP | no. | 1
c | Supplying, installing and commissioning a firebox containing a roller and a long rubber hose of 30m | no. | 1
d | Supplying and installing and commissioning press steel tyip water tank with thickness of 5mm and combines 20 cubic meter | m³ | 1
e | Supplying, installing and commissioning galvanized steel pipes with a diameter of 3" | L.S | 1
f | Concrete base for the tank and pump (LXW) The price include formwork, concrete and one layer of 12 mm steel bars | L.S | 1
g | Steel cage for the pump | L.S | 1
89 | Fire Alarm System Supply, install, connect and commission water fire alarm system with following details. The price include all material, accessories and work necessary to complete the work and have fully functional system
a | Intelligent adressable fire alarm control panel 4 loop | L.S | 1
b | Intelligent adressable optical smoke detector | no. | 1
c | Intelligent adressable optical heat detector | no. | 1
d | Adressable manual call point | no. | 1
e | Fire alarm system sounder | no. | 1
f | Fire alarm system Strobe | no. | 1
g | Indoor type fire alarm cable cable size (1 pair x 1mm) | m.l | 1
h | PVC pipe with fittings | m.l | 1
90 | "Wireless Fire alarm control panel: consist of 4 zones, with UPS and batteries to work during shutdawn the electrcity power, with covering all detectors & consists of the latest dual flash-based microprocessor technology combined with a high resolution, high contrast, graphical LCD display and tactile keypad providing a simple select and click programming aid for engineer configuration and end-user operation." | no. | 1
a | Intelligent wireless Smoke Detector. | no. | 1
b | Intelligent wireless heat Detector. | no. | 1
91 | Firefighting System (type FM200): Supply, install, connect, design and test complete automatic firefighting system, English origion or equivlent, the system should suitable for Iraq weather (high temperture and dust). Price includes supplying, laying, installing, testing, commissioning, necessary cutting, drilling to complete works as required. the below is the major items:
a | Combined fire Extinguishing control panel: consist of 2 zones, with UPS and batteries to work during shutdawn the electrcity power, with covering all detectors & consists of the latest dual flash-based microprocessor technology combined with a high resolution, high contrast, graphical LCD display and tactile keypad providing a simple select and click programming aid for engineer configuration and end-user operation. | no. | 1
b | Gas abort. | no. | 1
c | Gas release. | no. | 1
d | Smoke detector. | no. | 1
e | Sounder & flasher. | no. | 1
f | Nozzle. | no. | 1
g | 50 kg FM200 set with all accessories. | no. | 1
h | Galvanized pipe 1'', with all required accessories. | m.l | 1
i | Wires 1 mm² lying through metal flexible pipes, the wires and the pipes type heat resistant. | m.l | 1
92 | Diesel Generator () kVA: Supplying, installing, connections, test of diesel engine generator as below size KVA prime Power), output 400/230 V, 3-phase, 4-wire, 50 Hz, 1500 RPM,intake air temperature of 50 °C at 0.8 power factor, full automatic (auoto run)with all mechanical and electrical connection by ATS and Control System, (Sound and weatherproof enclosure). the Price includes supplying, installing, test, connection and all connections of fuel pipes and exhaust, test and commission, necessary cutting, drilling and (cable termination with Cu lugs) to complete works as required also the spare parts include 1-Oil filter /10 No. 2-Fuel Filter/5 No. 3-Air filter /3No. All needed works to complete the job, shall be included within the price.
a | 5 KVA | No. | 1
b | 10 KVA | No. | 1
c | 20 KVA | No. | 1
d | 30 KVA | No. | 1
e | 45 KVA | No. | 1
f | 65 KVA | No. | 1
g | 100 KVA | No. | 1
h | 150 KVA | No. | 1
j | 200 KVA | No. | 1
k | 250 KVA | No. | 1
l | 300 KVA | No. | 1
m | 450 KVA | No. | 1
n | 500 KVA | No. | 1
o | 650 KVA | No. | 1
p | 750 KVA | No. | 1
q | 1000 KVA | No. | 1
93 | External Fuel Tank with Base: Supply of materials, tools and manpower for installing galvanized water tank of 1400 liters. Cylindrical shape and with plate gauge 16(1.56mm), supported by base, including the connection of the inlet and outlet pipes. The price of work includes all piping and fittings, valves, float valves, accessories. All needed work to complete the job will be included within the price. a) steel base made of iron angles 50*50*3mm., with anti rust paint and three layers of oil paint. b) level monitor (oil proof). The price shall includes fittings, necessary accessories and all needed works to complete the job. All needed works to complete the job, shall be included within the price. | N0. | 1
94 | ATS Automatic transfer switch (below KVA) Supply and install ATS Automatic transfer switch (the board weather proof type), the ATS power must to carry out load for generator (as below KVA), the price include guages, busbar, light indcatores and all required accessoires, all ATS components from ABB, Schneider, or equivalent. All works according to the supervisior enginner, all works are requirements to complete the job.
a | 65 KVA | No. | 1
b | 100 KVA | No. | 1
c | 150 KVA | No. | 1
d | 200 KVA | No. | 1
e | 250 KVA | No. | 1
f | 300 KVA | No. | 1
g | 450 KVA | No. | 1
h | 500 KVA | No. | 1
j | 650 KVA | No. | 1
k | 750 KVA | No. | 1
l | 1000 KVA | No. | 1
95 | Busbar Board: Supply, tools, materials, and manpower to install a 3ph busbar board, with suitable for at least 100 amp and higher, the board should a weatherproof, metal board. The price include a cable terminal, Tape, cooper luges, any need to complete the job. | No. | 1
96 | AC VRF System (10 Ton): Supply, install, connect, and commission vertical Split unit Air-conditioning inverter type (Cool & Heat) of overall capacity of 10ton (2 compressors at minimum), (120,000 btu), Technical specification and Type of compressor T3, Type of refri. gas(R410a) includes all wiring/connecting with necessary size PVC isolated copper cable/wires laid inside existing concealed PVC pipe and if required laid through new surface PVC pipe (Or trunks) with switches and all accessories. The price includes supplying, installing, connecting, laying, drilling & cutting, and commissioning to complete works as required. All needed work to complete the job will be included in the price. The price includes supplying and installing the indoor units (6 units of 2-ton Capacity Each). The Number of indoor units may be changed but the overall capacity must remain the same. The indoor units might be (wall mounted, Ceiling suspended or Cassette; Four ways, two ways or way). It might also require to be deductible, high static units. The price also include central remote control system. The price also include Supply and installation of All refrigerant piping, pipe fittings, splitters, Gas Charging, SI angles/ flats supports, accessories, minimum 19mm thick Class O Nitrile Rubber Insulation for entire piping system, Refrigerant piping should be additionally insulated with factory laminated 200 GSM glass cloth for UV and mechanical protection and manufacturer recommended adhesive (solvent-free) sealant applied at all joints. Refrigerant pipes on terrace or platform shall be installed on raised GI Cable tray and finally covered with GI Sheet Cover for protection. Rates should include the same. Along with 19mm O class Nitrile insulation and supports, indoor & outdoor units duly insulated. All piping inside the room in ceiling shall be properly supported in cable tray. | no. | 1
97 | Computer Servers: 1. Server Type: DELL EMC (or equivalent) POWEREDGE R940 8 X 2.5 INCH RECERTIFIED SERVER 2. Processor(s): 2 X INTEL XEON GOLD 16 CORE PROCESSOR 6130 2.10GHZ 22MB L3 CACHE TDP 125W 3. Memory: 24 X 64GB PC4-21300 DDR4-2666V-L LOAD REDUCED ECC MEMORY 4. Hard Drive: 10 X DELL 1TB 15K RPM 2.5 INCH 12G SAS HARD DRIVES 5. Drive Bays: 8 X 2.5 INCH SFF DRIVE BAYS 6. Raid Controller: PERC H330 12GB/S RAID CONTROLLER 7. Networking: INTEL I350 1GB QUAD PORT NETWORK DAUGHTER CARD 8. Power Supply: 2 X 1100W POWER SUPPLY 9. 4 X Tripp Lite Heavy-Duty Power Extension Cord 15A 10. Rack Mount Universal Rail 1U. 11. Windows Server 2022. Patch Panel 1- 48-Port Cat6 Unshielded Patch Panel, Wall mount or Rackmount. UPS 1. 2200VA Smart UPS with SmartConnect, SMC1000-2UC Rack Mount UPS Battery Backup, Sinewave. Console 1. Rack Mount Console¦ 1U LCD Tray ¦ 18.5” LCD Widescreen¦ 1600 X 1200 Resolution Switches & Routers 1- C1000-24T-4G-L - Cisco Catalyst 1000 Series Switches. Server Rack Cabinet 1- 22U Server Rack Cabinet with secure locking door - 4 Post Adjustable Depth (5.5" to 28.7") - 19-inch Portable Network Equipment Enclosure on wheels/casters. | no. | 1
| TOTAL |  |  | 0

## Agricultural Woks
AGRICULTURAL WOKS
# | Item Description | Unit | Qty | Price $
1 | Soil for grass and tree: Supply of materials, tools, and manpower to provide garden soil as required depth clear from organic materials and suitable for evergreen grass, pure and fine sand, including leveling with required thickness with all required work. | m³ | 1
2 | Soil Supply Supply of materials, tools, and manpower to supply and laying sandy soil "known locally زميج" of 40 cm depth. The price includes leveling the ground to prevent rain water from accumulating in the park. | m³ | 1
3 | Pre-germinated grass: Suplying and Grassing with specified grass As below required, including watering and maintenance of the lawn for 30 days or more till the grass forms a thick lawn free from weeds and fit for mowing including supplying good earth if needed. All needed work to complete the job will be included within the price.
a | Shade grass | m² | 1
b | Calcatta doob | m² | 1
c | indian grass | m² | 1
4 | Plant grass by seeds: Suplying and plant seeds grass with specified grass As required, including watering and maintenance of the lawn for 30 days or more till the grass forms a thick lawn free from weeds and fit for mowing including supplying good earth if needed. All needed work to complete the job will be included within the price.
a | Shade grass | m² | 1
b | Calcatta doob | m² | 1
c | indian grass | m² | 1
Planting shrubs
5 | Supply of materials, tools, manpower and planting Myrtus communis seedlings, with hight not less than 80cm. The price includes all work requirements and as directed by the supervising engineer. | no. | 1
6 | Planting Tree: Supply and plant trees (according to the below types) according to approved locations inside the garden by the engineer with a minimum (clear trunck height 2 m without leaves and root), Price includes excavation filling agricultural soil, support and mulch wherever needed according to design drawing and engineers instruction.
6.1 | Acacia tree with flowers, 3m hight, 3 years old. | no. | 1
6.2 | Acacia trees, 3m length, 3 years old | no. | 1
6.3 | Ailanthus altissima, 3 m hight, 3 years old | no. | 1
6.4 | Albizia julibrissin 3m hight, 3 years old. | no. | 1
6.5 | Albizia julibrissin 3 meters high, 3 years old | no. | 1
6.6 | Bottle Brush tree , 3 meters, 3 years old | no. | 1
6.7 | Casuarina 3 years old and 3 m Hight | no. | 1
6.8 | Citrus aurantium 3 years old, 3 m, Hight | no. | 1
6.9 | Crimson Bottlebrush, 3m hight, age 3years. | no. | 1
6.10 | Cupressus 3m hight, 3 years old | no. | 1
6.11 | Cupressus sempervirens 3years old, 2m Hight | no. | 1
6.12 | Dodonaea with height 1m, 2 years old | no. | 1
6.13 | Duranta Erecta, 3m hight, 3 years old | no. | 1
6.14 | Eucalyptus 3 years old (3 meters) | no. | 1
6.15 | Euonymus japonicus 2m,3years old | no. | 1
6.16 | Flame bottletree, 3m length, 3 years old | no. | 1
6.17 | Grafted Robinia with 3m length, and 3 years age. | no. | 1
6.18 | Hibiscus rosa-sinenis, 3 m hight, 3 years | no. | 1
6.19 | Jacaranda mimosifolia, 3m hight, 3 years old. | no. | 1
6.20 | Lagerstromia indica, 3m hight, 3 years old | no. | 1
6.21 | Melia azedarach 3m hight, 3 years old. | no. | 1
6.22 | Olive tree 3m height, 3 years old. | no. | 1
6.23 | Olive trees, 3m height, 3 years old. | no. | 1
6.24 | Palm tree 3m hight, 4 years | no. | 1
6.25 | Pinus pinea 3m height, 3 years old. | no. | 1
6.26 | Racosperma 3 m, 3 years old | no. | 1
6.27 | Robinia pseudoacacia 3m hight, 3 years old | no. | 1
6.28 | Schinus molle, 3m length, 3 years old | no. | 1
6.29 | Tecoma Stans, length 3m, 3 years old | no. | 1
6.30 | Tuya Holmstrup, 3m hight, 3 years old. | no. | 1
3.31 | Washingtonia, 3m hight, 3 years old | no. | 1
Implanting Flowers Seedlings
7 | Supply of materials, tools, manpower and planting flowers seedlings with below types:
a | Aster | no. | 1
b | Begonia | no. | 1
c | Bougainvillea | no. | 1
d | Bougainvillea | no. | 1
e | Euonymus japonicus | no. | 1
f | Gazania | no. | 1
g | Gazania splendens | no. | 1
h | pelargonium | no. | 1
i | pelargonium | no. | 1
j | Red Rosa Damascena | no. | 1
k | Rosa Damascena | no. | 1
l | Rosa davidii seeds | no. | 1
m | Rosa 'Fifty Fifty', | no. | 1
n | seeds Woundwort | no. | 1
o | Turkish Rosa Damascena | no. | 1
CLIMBERS PLANTING WORKS
8 | Planting CLIMBERS by Digging holes (0.45 x0.45 x 0.45 ) in ordinary soil and refilling the same with the excavated earth mixed with manure in the ratio of 2:1 by volume, flooding with water, including removal of rubbish and surplus earth. | no. | 1
IRRIGATION WORK
9 | Supplying, Laying, Joining & Commissioning of Rigid LDPE pipe of following sizes with necessary fittings, adhesives etc. the work inculding digging trenches in all types of ground for laying done pipes preparing soft bedding for pipes, refilling etc. (Depth 450 mm & Width 300 mm) and according to the direction of the supervisor engineer.
a | LDPE Pipe 75 mm X 6 kg/cm² | m.l | 1
b | LDPE Pipe 63 mm X 6 kg/cm² | m.l | 1
c | LDPE Pipe 40 mm X 6 kg/cm² | m.l | 1
d | LDPE Pipe 25 mm X 10 kg/cm² | m.l | 1
e | LDPE Pipe 20 mm X 10 kg/cm² | m.l | 1
f | LDPE 16 mm Size / 2.5 Kg/cm² /with all necessary fittings likeVolve/bend/Joiner etc | m.l | 1
10 | Sprinkles System (USA origion or equal) for irrigation system: Supply of materials, tools and manpower for installing sprinkles system that coverd the required area with suitable diameter and rotation in 360°, including use a pice of pvc pipe 6" with length 20cm to put the sprinkler inside it, and all accessories, and fittings, valves, accessories, also with remove the old. All needed work to complete the job will be included within the price. | m² | 1
Green Houses
11 | Iron structure: Dimensions: 51.5mX9mX3.25m, Iron thickness 1.5-2m, The diameter of curves should be 60m. Each Green House contain 22 curves the distance between each curve 2.5m except the first and last curves the distance is 2m. All parts of Green House should be electrically galvanized. All parts should be connecting to each other by crosses,(All crosses are made from 55mm diameter and 2mm in thickness galvanized pipes, the ground crosses should be 25-30cm in length. The steel structure includes all the brackets and parts required to connect the structure together, including arcs, tubes, crosses and all the other required items. | no. | 1
12 | Doors: The Green House should contain 2 doors, each door contains 2 parts with dimensions (3mX2.5m), doors iron is 32ml galvanized electrically. Provide 4 pieces of galvanized iron pipe 32ml to be used as a stand to hold the doors when opened. The nylon should tie to the iron by clips not wire | no. | 1
13 | Nylon Cover: The nylon thickness is 200microns, the dimensions are (5.5mX56m) ,Yellowish or green colour (transparent), have UV not less than 5%, the light transmittance should be 85%. light distribution 45% - Anti-cracking by UV at least 5-9%. 3 rolls for each greenhouse, have at least 3 years guarantee and Europe Origin.Wherever the nylon is tied with iron it must be tied by clips not wire. | no. | 1
14 | Nylstrong: should be 2.6-3ml in thickness, white colour, 38 lines(2000m length) per Green House, and Europe origin and have at least 3 years guarantee | no. | 1
15 | Seedlings holder wire: The thickness should be 2.5ml, galvanized, (10 lines per green house).550 m.l | no. | 1
16 | Rope for hooking seedlings: 5 KG of special rope for each green house | no. | 1
17 | Mesh for covering doors and all openings sides.Green or white colour, 5X50m | no. | 1
Hand Tools
18 | Shovel with Wooden Handle | no. | 1
19 | Spade Shovel (Sharpen iron Shovel) | no. | 1
20 | Metal Rake with Wooden Handle | no. | 1
21 | Wheelbarrow with good wheel colored with anti-rust | no. | 1
22 | Mattock wooden handle | no. | 1
23 | Pick -axe with wooden handle | no. | 1
24 | Knapsack sprayer capacity | no. | 1
25 | Watering can 5LTR | no. | 1
26 | Arch Saw to cut Pipe 2“ | no. | 1
27 | Drill Hole puncher for irrigation pipe | no. | 1
28 | Drip irrigation pipe cutters 20mm Full metal construction, Anti rust, Safer than using a knife, Provides straight cuts to ends of plastic pipe | no. | 1
29 | Gloves | no. | 1
30 | Medium sickle Wooden Handle 34 cm | no. | 1
31 | Small Hand trowel length 29 cm width 9 cm | no. | 1
32 | Small Garden Rake | no. | 1
33 | Small Mattock | no. | 1
34 | Mask ( face mask 50 in pack) | no. | 1
Irrigation System
35 | Main pipe High density polyethylene (HDPE)10 bar, 50mm diameter. | m.l | 1
36 | Metallic (Or Plastick polyethylene) Water Tank 2-3mm thickness, capacity (2000 lt), the size of the inlet and outlet 2'', with all required fittings (GI nipple 2''x1, HDPE valve 2''x1, GI elbow 2''x1). | no. | 1
37 | Irrigation GR Pipe 16mm Diameter, 10 lines for each green house, distance between each two nozzles is 40cm. One roll 400 m. | Roll | 1
38 | Saddles (50mmx3/4'') | no. | 1
39 | Small plastic valve (3/4''x16mm) | no. | 1
40 | Galvanized Valve 50mm | no. | 1
41 | End line for pipe 50mm | no. | 1
42 | Elbow HDPE 50mm | no. | 1
43 | disk filter 50mm | no. | 1
44 | Starting line female threaded 50mm | no. | 1
45 | starting line male threaded 50mm | no. | 1
46 | End line for GR pipe 16mm in diameter | no. | 1
47 | Clips 20mm | no. | 1
48 | Fertilizer tank 60 liter, thermal painted with all necessary accessories to be connected to the main 50mm HDPE pipe line | no. | 1
49 | Decorative colored Stone/Gravel Supply of materials, tools, and manpower to place decorative colored stone and colored gravel in the places shown in the drawings and around tress. The thickness is 15 cm, size of stone/gravel range (3-6cm). All needed work to complete the job will be included within the price. | m² | 1
50 | Anti-Weed Nonwoven Geotextile Supply of materials, tools, and manpower to lay Anti-Weed Nonwoven Geotextile (Permeable) )according to the supervising engineer's instructions. All needed work to complete the job will be included within the price. | m² | 1
51 | Concrete Tiles Supply of materials, tools, and manpower to place concrete tile with dimension of (60 cm x 60 cm). The price include cutting with grinder if needed. The tile is used to be place over the decorative stones in the garden. | no. | 1
| Total |  |  | 0

## Steel structure
STEEL STRUCTURE
# | Item Description | Unit | Qty | Price $
1 | Anchur Bolt: supply and provide all materials to cast Anchore bolts inside pedistal concrete including leveling connecting with steel reinforced with required overlap length according to supervisor engineer.
1.1 | Ø 25mm @80cm length | No. | 1
1.2 | Ø 25mm @50cm length | No. | 1
1.3 | Ø 20mm @80cm length | No. | 1
1.4 | Ø 20mm @50cm length | No. | 1
1.5 | Ø 16mm @80cm length | No. | 1
1.6 | Ø 16mm @50cm length | No. | 1
1.7 | Ø 12mm @50cm length | No. | 1
2 | Base: plate: Supply install and level base plate with anchur bolts
2.1 | LXDXT (40X40X2)cm | No. | 1
2.2 | LXDXT (40X40X3.2)cm | No. | 1
2.3 | LXDXT (30X30X3.2)cm | No. | 1
2.4 | LxDxT (20X20X2) cm | No. | 1
2.5 | LxDxT (60X60X3.2) cm | No. | 1
2.6 | LxDxT (60X60X4) cm | No. | 1
3 | Steel Columns & Beams Sections: Supply and install new steel sections for columns and beams, including welding, bolts, fixing and and support sections, painting with 2 layers of fire resistant paint class F90 ( 90 minutes and all required work), with all required work.
3.1 | IPE 80 | m.l | 1
3.2 | IPE 100 | m.l | 1
3.3 | IPE 120 | m.l | 1
3.4 | IPE 140 | m.l | 1
3.5 | IPE 160 | m.l | 1
3.6 | IPE 180 | m.l | 1
3.7 | IPE 200 | m.l | 1
3.8 | IPE 220 | m.l | 1
3.9 | IPE 240 | m.l | 1
3.1 | IPE 300 | m.l | 1
3.11 | IPE 330 | m.l | 1
3.12 | IPE 360 | m.l | 1
3.13 | IPE 400 | m.l | 1
3.14 | IPE 450 | m.l | 1
3.15 | IPE 500 | m.l | 1
3.16 | IPE 550 | m.l | 1
3.17 | IPE 600 | m.l | 1
3.18 | HEA 80 | m.l | 1
3.19 | HEA 100 | m.l | 1
3.2 | HEA 120 | m.l | 1
3.21 | HEA 140 | m.l | 1
3.22 | HEA 160 | m.l | 1
3.23 | HEA 180 | m.l | 1
3.24 | HEA 200 | m.l | 1
3.25 | HEA 220 | m.l | 1
3.26 | HEA 240 | m.l | 1
3.27 | HEA 300 | m.l | 1
3.28 | HEA 320 | m.l | 1
3.29 | HEA 360 | m.l | 1
3.3 | HEA 400 | m.l | 1
3.31 | HEA 450 | m.l | 1
4 | Install purlin steel section for roof and walls to be install @100 cm c/c above the main steel beam for fixing the sheet roof, including welding and all required work
4.1 | Steel Hollow sections (100x50x2mm ) | m.l | 1
4.2 | Steel hollow sections (80x40x2mm) | m.l | 1
4.3 | Steel L section (100x100x4mm) | m.l | 1
4.4 | Steel L section (80x80x2mm) | m.l | 1
5 | Sandwich panel: Supply and install new sandwich panels for roof and walls, including screwing, fixing and all required work and covering top joints using galvanized plate of 60cm, 2mm thick to be fixed above sandwich panel (sandwich specifications: fire rated sandwich panel, according to the BS EN ISO 1182 2020 Code or equivalent) Polyurethane (PUR) Insulated Sandwich Panel. External Sheet: 0.5mm thick, galvanized sheet + protective foil. Internal Sheet: 0.45mm thick, galvanized sheet + protective foil. Density: Polyurethane insulated with 38-42 kg/m³ (standard) density -Compressive strength ≥0.06 Mpa -Tensile strength ≥0.04 Mpa -Shear strength ≥0.05 Mpa - Width Of Panel : 1000 mm Contractor should ensure the proper sealing and check for leakages. Roof edges shall be finished with metallic flashings.
5.1 | 5 cm thickness | m2 | 1
5.2 | 10 cm thickness | m2 | 1
Sunshade (K-span type and corrogated metal sheet) steel
1 | Steel columns : supply and install new steel sections for columns for sunshade
1.1 | Square hollow sections : (100x100x3mm) | m.l | 1
1.2 | Square hollow sections : (80x80x3mm) | m.l | 1
1.3 | Square hollow sections : (100x100x2mm) | m.l | 1
1.4 | Square hollow sections : (80x80x2mm) | m.l | 1
2 | Steel beams : supply and install main beams for the sides of k-span
2.1 | Square hollow sections : (100x100x3mm) | m.l | 1
2.2 | Square hollow sections : (80x80x3mm) | m.l | 1
2.3 | Rectangular hollow sections : (100x50x3mm) | m.l | 1
2.4 | Rectangular hollow sections : (80x40x3mm) | m.l | 1
2.5 | Square hollow sections : (100x100x2mm) | m.l | 1
2.6 | Square hollow sections : (80x80x2mm) | m.l | 1
2.7 | Rectangular hollow sections : (100x50x2mm) | m.l | 1
2.8 | Rectangular hollow sections : (80x40x2mm) | m.l | 1
3 | K-span metal sheet: Supply and install corrugated metal sheet thickness (AS BELOW) fixed by screws and overlapped to prevent water leakage. The price includes water drainage & roof drainpipe system according to specifications, and to the instructions of site engineer.
3.1 | thickness 0.5 mm | m2 | 1
3.2 | thickness 0.7 mm | m2 | 1
4 | Corrugated Sheet: Supply of materials, tools and manpower to install new corrugated metal sheet with new corrugated metal sheet, fixing with frame by screws and overlapped in order to prevent water leakage and Painting the steel structure with one layer of anti rust and two layers of oil paint, Also remove all damaged frame and corrugated sheet to a site approved by local authorities. All needed work to complete the job will be included within the price.
4.1 | thickness 0.5 mm | m2 | 1
4.2 | thickness 0.7 mm | m2 | 1
5 | Portal Frame (LxW)m (Warehouse): Supply of materials, tools and manpower to install a portal frame (Workshop) of (LxWm) with height 9m in the middle and up to 5.5m in the sides from the finishing floor level. The price includes providing: 1-Anchor bolts of diameter 25mm and length of 80cm (hooked end) (4) anchor bolts per steel column. 2-Base plate (500x500x25)mm per steel column. 3-Steel columns of section (IPE 400). 4-Steel rafter beams of section (IPE 330). 5-Steel purlins of section (UPE 120) every 80cm c/c. 6-Steel bracing for the roofs and the walls of section (UPE 120). 7-Cover the warehouse with corrugated metal sheet thickness 1 mm and (15%) should be covered with transparent poly-carbonated sheet 1 cm for lighting. 8-Painting the steel structures with one layer of anti rust and two layers of oil paint. 9-The measurement should be the horizontal projection of the steel structure (i.e. L mxW m = Aera m2). All needed work to complete the job will be included within the price. See attached drawings | m2 | 1
6 | Machinery Parking Sun Shed (WxLxH4): Supply of materials, tools and manpower to removed the existing damaged sun shade and manufacturing new sun shade. The price includes: 1-Excavation for the columns footing (60x60x60cm). 2-Providing (4) anchor bolts of Ø16mm and length of (40cm) for each column. 3-Casting concrete (C25MPA) with Providing and installing base plate of (250x250x10mm) for each column. 4-Providing columns of steel square tube 100x100x3mm with height 4 m (Spaced 6 m in Y-direction and 3 m in X-direction). 5-Sun shed main steel beam using section 100x100x3mm to be fixed between all columns for both directions. 6-Steel Purlin using rectangular steel section 100x50x3mm and spaced 80 cm c/c. 7-Corrugated galvanized sheet thickness 0.5 mm, fixed by screws and overlapped in order to prevent water leakage, adding 50 cm for all sides as dimensions. 8-Painting the whole structure with (2) two-layers of anti rust paint and (3) three-layers of oil paint. The price also includes testing the water leaks, sealing, scaffolding installation, dumping of all debris to a site approved by local authorities,The price includes water drainage & roof drainpipe system according to specifications, in case it is needed, as well as all needed works to complete the job. SEE ATTACHED DRAWING.
6.1 | Corrugated galvanized sheet thickness 0.5 mm | m² | 1
6.2 | Corrugated galvanized sheet thickness 0.7 mm | m² | 1
7 | Sun Shed (LxWm) with Concrete Floor for Generator : Supply of materials, tools and manpower to install sun shed. The price includes: 1-Excavation for the columns footing (60x60x60cm). 2-Providing (4) anchor bolts of Ø16mm and length of (40cm) for each column. 3-Providing base plate of (250x250x10mm) for each column. 4-Casting column footing (60x60x60cm) using (C25MPa) concrete and sulphate resistance cement for each column. 5-Providing columns of steel square tube 100x100x3mm with height 4m (Spaced 4.0m in X-direction and 5.0m in Y-direction). 6-Providing main beams of steel square tube 100x100x3mm. 7-Providing purlin of rectangular steel tube 100x50x3mm and spaced 80cm. 8-Corrugated metal sheet thickness 1mm, fixed by screws and overlapped in order to prevent water leakage. 9-Providing BRC Fence (100x100x4mm) and 3.0m height and using steel angle 50x50x3mm as braces and steel door (1×2 m) by using BRC (50x50x4mm) and steel angle 75x75x3mm, 50x50x3mm and 38x38x2.5mm.The price of works includes door lock, handle. 10-Painting the steel structure with one layer of anti rust and two layers of oil paint. 11-Casting (15cm) thickness concrete with BRC (150x150x5mm) using (C25MPa) concrete and sulphate resistance cement for the sun shed floor. All needed work to complete the job will be included within the price. See attached drawing#42. | m2 | 1
8 | Repair Sunshade: Supply of all necessary materials, tools and manpower to repair the damaged sun shade.The work includes steps as below: 1- Remove the damaged corrugated galvanized sheet. 2- Repairing all the existing steel structure by welding and adding steel sections. 3- Install new corrugated galvanized sheet 0.6 mm thickness, using proper sealant screws. 4- Cleaning the steel surface from old paint and rust, Then paint with two layers anti-rust paint and three layers of oil paint. The price also includes testing the water leaks, sealing, scaffolding installation, dumping of all debris to a site approved by local authorities,The price includes water drainage & roof drainpipe system according to specifications, in case it is needed, as well as all needed works to complete the job. | m² | 1
9 | Tensile Fabric roofing over courtyard (Sunshade): Provision of materials, labour, equipment and all other necessary requirements for installing fabric sunshade. 100% pure polyester outdoor fabric with double threaded seams on the edges, to include stainless steel D rings and 1.5m nylon drawstring at each corner. The fabric to be both block UV in addition to being waterproof, a waterproof coating is pre-applied to the fabric as per manufacturers detail. Stainless steel fixing kit to be supplied and installed. Size to be determined onsite. All works according to instructions of the supervisor engineer. | m² | 1
10 | Portal Frame (Sun Shed) on the roof: Supply of materials, tools and manpower to install (on the existing roof) a portal frame (sun shed) of with height 3m in the middle and 2m in the sides. The price includes providing: 1-Anchor bolts of diameter 20mm and length of 60cm (hooked end) (4) anchor bolts per steel column. 2-Base plate (400x400x20)mm per steel column. 3-Steel columns of section (IPE 330). 4-Steel rafter beams of section (IPE 270). 5-Steel purlins of section (UPE 100) every 80cm c/c. 6-Steel bracing for the roofs and the walls of section (UPE 100). 7-Cover the sun shed with corrugated metal sheet thickness 1 mm. 8-Painting the steel structures with one layer of anti rust and two layers of oil paint. 9-The measurement should be the horizontal projection of the steel structure (i.e. 45mx14m = 630 m2). All needed work to complete the job will be included within the price. See attached drawings#24,25,26,27,28. | m² | 1
Steel Structure and Sandwich Panel works
11 | Steel Structure and Sandwich Panel ( Walls and Roofs ): 1-Steel columns (100mmx100mmx5mm)( height (3.8-4.0)m. The columns should be provided and installed at the intersections, corners of all the walls and where required for the wall its length exceeding 5m. 2-Main beam truss (100mmx100mmx3mm) to be placed to installed to connect all the column lines. 3- purlins (100mmx50mmx3mm) (spaced @ 0.8 m c/c). 4-The steel columns will be completely welded in steel plate (200mmx200mmx10mm) having 4 holes 16mm diameter to be fixed on the footing plates with nuts. 5-The steel plate will be fixed in concrete using 4 welded bolts bars 16mm diameter and 200mm embedded length and 70mm upper screw for fixing columns. 6-Install channel-shape( 2mm thickness) under and above walls, around the door and windows openings to fixing the sandwich panel. 7-X-bracing section angle 70mmx70mmx7mm in the roof steel structure at first panel and last panel to withstand against lateral force of wind pressure and same type of bracing between first and last columns rows at short direction. 8-All steel sections shall be painted by one layer of anti-rusted paint and 3 layers of oil paint with pistoled before being mounted Roof. 9-Installation of sandwich panel (roof and external walls) best quality, 5 cm thickness, density 16-24 kg/m3, load bearing capacity 1.00 kN/m2, K-value 0.32 W/m2K(resistant fire type, according to the BS EN ISO 1182 2020 Code or equivalent) , fixed by screws and overlapped in order to prevent water leakage . 10- Installation of sandwich panel ( internal partition), 5 cm thickness, density 16-24 kg/m3, K-value 0.55 Wm2K(resistant fire type, according to the BS EN ISO 1182 2020 Code or equivalent), fixed by screws and overlapped in order to prevent water leakage and fill the joints between the sandwich panels and the joints between the walls and the floor by silicone material.11-Rain water drainage and cover joint on top ( galvanized sheets Cage 16 ) and cover joint on top with rain water pipes 3in diameter each 4 meters.All needed work to complete the job will be included within the price.See attached drawing#38. | m² | 1
12 | Fabricate WC Cabin Supply and install Fabricate WC Cabin L*2.5m consists of WCs (1.2*1.2m), the high cabin is 2.6m with 10cm legs above iron plate 50*50cm, from sandwich panel 5cm thickness smooth type for the walls and corrugated type for the ceilings (extended 30cm for all sides), according to the following specifications. A- Steel frame from, 10*10cm *3mm columns, with 5*10cm*0.3mm ceiling and 10*5cm *3mm bottom with each 60cm intervals in both directions, and 1.5" steel angle to fix the sandwich panels walls and frames for windows and doors. frame painted well using anti-rust paint and three layers of oil paint. B-Cabin has doors PVC 2*1m (clear width 90cm)for eachWCs (1.2*1.2m), completely with locks and accessories, good quality, and good fixing and frames. C- Cabin has (50*50cm) windows vertically open with insect mesh for eachWCs (1.2*1.2m), according to drawings with 6" exhaust fans for eachWCs (1.2*1.2m). and including single glass 4mm for all windows, good quality. D- Supply and install 1 circular downlights LED 18w for inside WC Cabin for eachWCs (1.2*1.2m), and 2 pcs 30w LED wall light waterproof for outside all of them supplied by 2*1.5mm wires Turkish type inside cable trays, with required electrical switches best type E-Supply and install 13A socket good type 2 pcs for WC cabin, supplied by 2*2.5mm wires inside cable trays, outdoor waterproof with all accessories F- Supply and install 2 circuit breakers good quality 25A, outdoor waterproof with all accessories for the WC cabin G-Supply and install steel checker plate for the floor of WC cabin good quality 2mm thickness or more H-Supply and install W.C seats eastern with a flush tank for eachWCs (1.2*1.2m), Turkish type with all accessories including, Guile, Manholes, and Drainage pipes to the Septic tank at site, tapes, and all needed to complete toilets I- Supply and install one suspended wash basin 40*60 cm with mixer gear type Turkish brand for each 4m2 area and piping with all accessories. including drainage system 2.5" PVC pipes to the septic tank at the site. | m² | 1
13 | Standard traffic signs: Supplying standard traffic signs according to the approved international specifications and various, warning, preventive, and regulatory types made of aluminum with a thickness of not less than 2 mm with reflective adhesive stickers in the form of a beehive and of good origin and resistant to weather conditions with columns of 2.5 inch diameter and a thickness of not less than 2.9 mm in length 3 meters of aluminum, with caps and all work requirements for fastening, shapes, dimensions and content of the mark, as directed by the supervising engineer. | No. | 1
14 | Flag Pole (6m): Supply materials,tools and manpower to install new Flag pole, height 6m, using steel pipe Ø 2.5", 3 mm thickness, fixing on the ground above concrete base (60x60x60cm), concrete C21Mpa, above base plate (400x400x5mm) , with 4 anchor bolt Ø 16mm, each anchor bolt 40 cm length. Including purchasing new IRAQ flag size (1.2x1.8m). Price of the work shall include two (2) layers of anti-rust and three (3) layers of oil painting. All needed works to complete the job will be included within the price. | No. | 1
15 | Flag Pole (3m): Supply materials,tools and manpower to install new Flag pole, height 3m, using steel pipe Ø 2.5", 3 mm thickness, fixing on the ground by using base plate (300x300x4mm) and supported by using steel angle section 50x50x3mm. Including purchasing new IRAQ flag size (1.2x1.8m). Price of the work shall include two (2) layers of anti-rust and three (3) layers of oil painting. All needed works to complete the job will be included within the price. | No. | 1
Fence Works:
16 | Outside Steel Fence: Supply of materials, tools and manpower to instalation the steel fence according to the followings specifications main frame using steel tube square (50x50x2mm), internal steel tube square(30x30x1.8mm)@15cm,steel strip(diameter :15cm thickness 3mm) and CNC Plate from bottom thickness 2mm hight 30 cm.The price includes 2 layers anti rust and thermoplastic painting of oil. All needed work to complete the job will be included within the price.All needed work to complete the job will be included within the price. See attached drawings#39. | m.l | 1
17 | BRC Fence : Supply of materials, tools and manpower to install a fence made of BRC(LxLx4mm) and 3.0m height and using steel angle 75x75x3mm and 50x50x3mm. the work include: excavation, concrete footings, sub base below footings, support fittings , posts, rail, tension bars, brace bands, accessories All needed work to complete the job will be included within the price. See attached drawings
17.1 | BRC(100x100x4mm) | m² | 1
17.2 | BRC(50x50x4mm) | m² | 1
18 | Holland Mesh Fence Supply of materials, tools and manpower to install outside galvanized BRC fence 50x50x4mm, 1.2 height and strengthening withciclur tube iron 100x100x3 mm, the work include: excavation, concrete footings, sub base below footings, support fittings, posts, rail, tension bars, brace bands, accessories All needed work to complete the job will be included within the price.The price also inclue painting the steel. | m² | 1
Total