## Technical Sheet (3)
Technical Specification Sheet - Installation of RO system in Jubail
Fallujah City - Anbar Governorate
Program Name: |  | ARILA - Assisting Reconstruction and Improving Living Conditions in Anbar
Project No.: |  | 21.1811.5-002.00
Project Name: |  | Installation of RO system in Jubail - Fallujah
CoSoft No.: |  | 83446018
Trade: |  | Construction works
Location: |  | Fallujah - Anbar
Technical Sheet
Item # in BOQ | Item Description | Technical Description | Standard specifications | Offered Specifications
3.01 | PVC Pipe of 2 inch diameter | Origin
Brand
|  | Year of manufacturing | 2022 or higher
|  | Weight of the pipe (kg/m) | 1.14
|  | Material density (Kg/m3) | 1330 to 1460 Kg/M3
|  | Thickness of pipe (inch) | 0.218
|  | Pressure (bar) - working | 16 to 24
|  | Pressure (bar) - testing | + 16
|  | Outside diameter (mm) | 2.375
|  | Is the certificate of origin available | Yes
|  | Will the pipe will be tested ? | Yes
|  | Period of warranty (Year) | One Year
4.01 | Raw Water Feeding Pump | Origin
Brand
|  | Discharge m3/h | 22
|  | Head m | 40 m
|  | Power | 4 K.W
|  | H.P | 5.5
|  | Impller | Stainless Steel (AISI 304)
|  | Shift | Stainless Steel (AISI 304)
|  | Case | Stainless Steel (AISI 304)
|  | Is the certificate of origin available | Yes
|  | Period of warranty (Year) | One Year
4.02 | Water Tanks | Origin
Brand
|  | Year of manufacturing | 2022 or higher
|  | Capacity / Liter | 10000
|  | Tank Plastic Type | HDPE / Food Type
|  | Period of warranty (Year) | One Year
4.08 | Anti-Scalant Dosing Pump | Origin
Brand
|  | Discharge l/h | 5
|  | Head m | 80
|  | Body | PVC
|  | Chemical Tank of 60 L | Inluded
|  | Is the certificate of origin available | Yes
|  | Period of warranty (Year) | One Year
|  | Period of warranty (Year) | One Year
4.09 | Anti-Chlorine Dosing pump | Origin
Brand
|  | Discharge l/h | 5
|  | Head m | 80
|  | Body | PVC
|  | Chemical Tank of 60 L | Inluded
|  | Is the certificate of origin available | Yes
|  | Period of warranty (Year) | One Year
4.10 | Chlorine Dosing Pump | Origin
Brand
|  | Discharge l/h | 5
|  | Head m | 80
|  | Body | PVC
|  | Chemical Tank of 60 L | Inluded
|  | Is the certificate of origin available | Yes
|  | Period of warranty (Year) | One Year
4.12 | Housing Membrane | Origin
Brand
|  | Model | BW 8040-2.
|  | Size | 2 elements/vessel
|  | Type | In/Out
|  | Made of | FRP Material
|  | Max Working psi | 450
|  | Is the certificate of origin available | Yes
|  | Period of warranty (Year) | One Year
4.13 | RO Membrane | Origin
Brand
|  | diameter | 8''
|  | length | 40''
|  | Removal recovery | 99%
|  | free chloride less or equal / ppm | 0.1
|  | Max Working psi | 600
|  | PH interval | 2-11
|  | Is the certificate of origin available | Yes
|  | Period of warranty (Year) | One Year
4.15 | Vertical Pump (High Pressure Pump) | Origin
Brand
|  | Discharge m3/h | 20 - 22
|  | Head m | 145
|  | Power Kw | 15
|  | H.P | 20
|  | Number of phases | 3
|  | Voltage | 380 to 400 V
|  | Impller | Stainless Steel (AISI 304)
|  | Shift | Stainless Steel (AISI 304)
|  | Case | Stainless Steel (AISI 304)
|  | Is the certificate of origin available | Yes
|  | Period of warranty (Year) | One Year
4.16 | Control Panel | Make: | Original manufacturer (Local Assembled Not acceptable)
|  | Brand | PLC, MEB, Contactors and the body of board
|  | Ambient temperature: | Maximum:55/C
Minimum:-10/C
|  | Relative Humidity : | around 60% at maximum temperature
|  | System Voltage : | 400V
|  | No of phase : | 3PH
|  | Frequency: | 50Hz
|  | Main MCCB breaker | 125 Amp
Rated Operational Current
|  | Enclosure | DKP steel, 2mm thickness , two doors
|  | Type | MCC type both for Electrical and Command control .
|  | Inner Materials | SIEMENS, Schneider , MG , ABB , or equivalent
|  | Protection class | IP 54
|  | Starting Device | Soft Starters
|  | Is the certificate of origin available | Yes
|  | Period of warranty (Year) | One Year
4.24 | CIP system for the backwash (with Pump) | Origin
Brand
|  | System Capacity m3/hr | 20
|  | Discharge m3/h | 22
|  | Head m | 40 m
|  | Power | 4 K.W
|  | H.P | 5.5
|  | No of phase : | 3
|  | Impller | Stainless Steel (AISI 304)
|  | Shift | Stainless Steel (AISI 304)
|  | Case | Stainless Steel (AISI 304)
|  | Is the certificate of origin available | Yes
|  | Period of warranty (Year) | One Year
4.25 | UV Sterilizer | Origin
Brand
|  | Housing Material | Stainless steel (304)
|  | Lumps | 4x55watt
|  | Power | 220watts
|  | AC | 220v
|  | Flow Capacity m3/hr | 10
|  | Is the certificate of origin available | Yes
|  | Period of warranty (Year) | One Year
4.26 | Ozone Generator | Origin
Brand
|  | Ozone Generator | 3gm
|  | Power | 60 W
|  | AC | 220-240 V
|  | Hz | 50 - 60
|  | Concentration Mg/L | 15-25
|  | External Case | Stainless Steel (AISI 304)
|  | Is the certificate of origin available | Yes
|  | Period of warranty (Year) | One Year
6.04 | AC / Split device 2 Ton Capacity | Origin
Brand
|  | BTU | 24000
|  | Type | Economic and environmental
|  | AC | 220-240 V
|  | Hz | 50 - 60
|  | Gas Type | R410
|  | Period of warranty (Year) | One Year
7.03 | Generator | Origin
Brand
|  | Type | sound insulated (canopied)
|  | Power / KV | 30
|  | AC | 400 V
|  | Hz | 50 - 60
|  | No of phase : | 3
|  | Earth system | Yes
|  | Is the certificate of origin available | Yes
|  | Period of warranty (Year) | One Year
8.01 | Solar Panels and System | Origin
Brand
|  | Type | PV
|  | Model | Crystalline
|  | Power / w | 545 half cut - mono
AC
Hz
|  | Invertor type | SUNNY TRIPOWER CORE1 or equivalent
|  | Invertor Kw | 8
Output
|  | No of phase : | 3
|  | Earth system | Yes
|  | Is the certificate of origin available | Yes
|  | Period of warranty (Year) | One Year
8.02 | Solar batteries | Origin
Brand
|  | Type | Lithium-ion, LiFeP04
|  | Cycles | 6000
|  | Power / KWh | 17.92
|  | AC | 48 V
|  | Nominal Capacity | 350 Ah
|  | DoD | More than 80%
|  | Is the certificate of origin available | Yes
|  | Period of warranty (Year) | One Year