## BoQ - Installation of RO system
BoQ - Installation of RO system in Jubail
Fallujah City - Anbar Governorate
Program Name: |  | ARILA - Assisting Reconstruction and Improving Living Conditions in Anbar
Project No.: |  | 21.1811.5-002.00
Project Name: |  | Installation of RO system in Jubail, Fallujah
CoSoft No.: |  | 83446018
Trade: |  | Construction works
Location: |  | Fallujah - Anbar
Cost Calculation
No. | Description | Qty. | Unit | Unit rate *) | Total Amount *) | portion
[---] | [---] | [---] | [---] | [USD] | [USD] | [%]
1.00 | Mobilization and Demobilization
1.01 | ! Remark - Contractor must put in consideration what necessary measures/items described below apply to the project ahead. Installation of the site office, provision of all construction equipment and plant, including water and electricity supply for all works, stores and materials (incl. disposal of waste) for the workers, removal of all rubbish and site preparation including demobilization. All costs pertaining to safety and security measures of site must be included. Any costs for site set up have to be included, no additional payment will be accepted. Use of existing construction equipment and plant, including water and electricity supply for all works, stores and materials (including disposal of waste) for the workers, removal of all rubbish and site preparation including demobilization. All costs pertaining to safety and security measures of site must be included. Any costs for site set up (where applicable) have to be included, no additional payment will be accepted. | 1 | Lump Sum |  | 0 | #DIV/0!
1.02 | Temporary Signs: Provision materials, tools and manpower to install temporary signage (W 190cm x H 90cm) printed on mounted plastic sheeting composite (As required by GIZ staff) fixed on tow steel legs (3” steel pipe diameter, 2m height) and all requirements to complete the job. | 1 | Pcs | 0 | 0 | #DIV/0!
1.03 | Permanent Signs: Provision materials, tools and manpower to install Permanent signage (W 100 cm x H 70cm) printed on mounted plastic sheeting composite (As required by GIZ staff) fixed on the face of the container with all requirements to complete the job. | 2 | Pcs | 0 | 0 | #DIV/0!
1.04 | Creation of an operation and maintenance plan for the maintenance of the RO system. This includes a cost and material plan. Training for maintenance technical personnel should be included. | 1 | Lump Sum | 0 | 0 | #DIV/0!
1.00 | Sub Total Mobilization and Demobilization |  |  |  | 0 | #DIV/0!
2.00 | Excavation and Backfilling
2.01 | Excavation works Supply materials, tools and manpower to excavate the pipeline path and trench in any soil with depth not less than 100 cm and 60 cm width, use of asphalt road cutting machine to cut the asphalt pavement layers of the streets, removing and cleaning the pipeline alignment from the accumulated water, with all requirement to complete the job and according to the supervisory committee instructions, | 40 | m3 | 0 | 0 | #DIV/0!
2.02 | Backfilling works - River sand Supply materials, tools and manpower to backfill a river sand layer which shall be clean of any organic materials, 30 cm thick on the top of the pipe and not less than 10 cm around other sides of the pipe, with all requirement to complete the job and according to the supervisory committee instructions | 10 | m3 | 0 | 0 | #DIV/0!
2.03 | Backfilling works - Clean Soil Supply materials, tools and manpower to backfill clean soil layer reaching the required level with well compacting it as a layers not more that 20 cm, the compaction percentage not less than 90% for each layer with all requirement to complete the job and according to the supervisory committee instructions | 30 | m3 | 0 | 0 | #DIV/0!
2.04 | Spreading a gravel layer Supply materials, tools and manpower to spread a 10 cm gravel layer for the area around the container and other the entrance, with all requirement to complete the job and according to the supervisory committee instructions | 18 | m3 | 0 | 0 | #DIV/0!
2.05 | Drilling Well Supply materials, tools and manpower to drill a well reaching the underground water, the price inculdes using of 4'' PVC pipes 10 bar inside the well and also iron cover for the well hole, with all requirement to complete the job and according to the supervisory committee instructions | 1 | l.s | 0 | 0 | #DIV/0!
2.06 | Demolish the exsisting wall Supply materials, tools and manpower to demolish the exsisting concrete block wall, according the work needs, the height of the wall 2.5 meter, with all requirement to complete the job and according to the supervisory committee instructions | 7 | m | 0 | 0 | #DIV/0!
2.00 | Sub Total Excavation and Backfilling |  |  |  | 0 | #DIV/0!
3.00 | Piping works
3.01 | UPVC & CPVC Water Pipes with Valves Supply, install, connect and test UPVC & CPVC Pipe Well Known brand, 16 bar and 25 bar according to need, with all accessories, in order to distribute and transport the water supplied from the water network to the water storage tanks, as per attached drawings and specifications, all installations and connections accessories Elbows, Tees, valves, reducers, connections, Washers.. etc. according to supervisory committee directions. The pipeline path should be approved by the end user before excavation process, and all the works required to complete the job. The required diameters sizes are as following: UPVC & CPVC Pipe of 2 inch diameter | 90 | m | 0 | 0 | #DIV/0!
3.02 | UPVC & CPVC Pipe of 1 inch diameter | 50 | m | 0 | 0 | #DIV/0!
3.03 | UPVC & CPVC Pipe of 3/4 inch diameter | 30 | m | 0 | 0 | #DIV/0!
3.04 | UPVC & CPVC Pipe of 1/2 inch diameter | 20 | m | 0 | 0 | #DIV/0!
3.00 | Sub Total Pipes works |  |  |  | 0 | #DIV/0!
4.00 | RO System
4.01 | Raw Water Feeding Pump Supply, install, and commission a horizontal shaft, multistage, centrifugal pump with its motor (Europe made), the hydraulic parameter (22 m3/hr, 4 bar), power: 4 KW, 5.5HP. The impeller, shaft, and the case should be stainless steel (AISI 304). The cable required to connect the pump to the RO board (Control Panel) is included. The cable should be running through conduit. All needed work to complete the job will be included within the price. | 1 | pcs | 0 | 0 | #DIV/0!
4.02 | Water Tanks Supply, install, and commission a 10000 liter water tank, to be installed and connected with the system, the work includes installation of two tanks for the raw water and two tanks for the filtered water, the prices includes installation of the tanks on steel structure, 1.5 meter height, constructed by squire steel sections of 3'' and 3mm, with making of X shape between the legs bottom and the top by using rectangular steel section 3X1.5'' and 3mm, also the price includes installation of four taps 3/4'' by using UPVC pipes and T shape from each filtered water tank, the tank shall be made of food grade HDPE, with all requirements to complete the job and according to the supervisory committee instructions | 3 | pcs | 0 | 0 | #DIV/0!
4.03 | Filtration - Sand Filter Supply and install FRP vessel/tank of sand filter (High quality brand). The dimension is 30"*72". Flow capacity 20-24 m3/hr. Control approach: Automatic control valves (made in Turkey) service and back-washing. The diffuser should be reinforced PP with 0.2 mm nozzles. piping 2" PVC. Test pressure 10 bar, and working pressure 4 bar. Back-wash time 10-15 min. Back-Wash flow 20 m3/hr. | 1 | pcs | 0 | 0 | #DIV/0!
4.04 | Sand Filter Media Supply, delivery and install 300 litter of sand; quartz and gravel the range of the sizes are, from bottom, 25 cm thick (9-6.5 mm) gravel, 25 cm thick (6.5-2.5 mm) gravel, 25 cm thick (2.5-1.5 mm) sand, 25 cm thick (1.5-0.6 mm) sand, with all requirements to complete the job, and according to the supervisory committee instructions | 300 | kg | 0 | 0 | #DIV/0!
4.05 | Filtration - Activated Carbon Filter Supply and install FRP vessel/tank of the activated carbon filter (high quality brand). The dimension is 30"*72"). Flow capacity 20-22 m3/hr. Control approach: automatic control valves (made in Turkey) or equivalent service and back-washing. The diffuser should be reinforced PP with 0.2 mm nozzles. piping 2" PVC. Test pressure 10 bar, and 4 bar working pressure. Back-wash time 8-10 min. Back-Wash flow 20 m3/hr. with all requirements to complete the job, and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
4.06 | Activated Carbon Filter Media Supply, delivery and install of 200 litter of sand, quartz and gravel, 100 litter activated carbon, with all requirements to complete the job, and according to the supervisory committee instructions | 300 | kg | 0 | 0 | #DIV/0!
4.07 | Automatic Valves for Filters Supply and connect, automatic control valves, Type: butterfly, Control Mode: Two Line – Two Control , Connection Method: Flange, Power: 220 VAC, Made: Asian or Europe, with all requirements to complete the job, and according to the supervisory committee instructions | 8 | pcs | 0 | 0 | #DIV/0!
4.08 | Anti-Scalant Dosing Pump Supply and install and commission a dosing pump - best quality brand, Italian. Hydraulic parameter 5l/hr, 8 bar, PVC body. The work includes supplying and installing chemical tank 60 L, high quality PVC. The electrical wiring included. with all requirements to complete the job, and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
4.09 | Anti-Chlorine Dosing pump Supply and install and commission a dosing pump - best quality brand, Italian. Hydraulic parameter 5l/hr, 8 bar, PVC body. The work includes supplying and installing chemical tank 60 L, high quality PVC.The electrical wiring included. with all requirements to complete the job, and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
4.10 | Chlorine Dosing Pump Supply and install and commission a dosing pump - best quality brand, Italian. Hydraulic parameter 5l/hr, 8 bar, PVC body. The work includes supplying and installing chemical tank 60 L, high quality PVC. The electrical wiring included. with all requirements to complete the job, and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
4.11 | Sediments Filter (Micron Filter) Supply and install a sediment filter with flow capacity 25 m3/hr and filtration capacity 5-micron, max pressure 6 bars. The work includes the stainless-steel housing of the filters with 15 filter pieces. The length of the filter is 40", PP type. with all requirements to complete the job, and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
4.12 | Housing Membrane Supply and install RO housing membrane (pressure vessel) model BW 8040-2. Size 2 elements/vessel. The type of the house in/out should be side type, made of FRP material. Max. working 450 psi. with all requirements to complete the job, and according to the supervisory committee instructions | 5 | pcs | 0 | 0 | #DIV/0!
4.13 | RO Membrane Supply and install RO membrane to be housed in the RO housing. The brand of the membrane should be Dupont Filmtec or equivalent (USA), diameter 8", length 40", removal recovery 99%, free chloride less or equal 0.1 ppm, max working pressure is 600 psi, PH interval 2-11. with all requirements to complete the job, and according to the supervisory committee instructions | 10 | pcs | 0 | 0 | #DIV/0!
4.15 | Vertical Pump (High Pressure Pump) Supply, install and commission vertical shaft, multistage centrifugal pump with its motor (Europe made).The hydraulic parameter Q:20 - 22 m3/hr; H:14.5 bar, power: 15 Kw, 20 HP, motor 3 Ph.,380-400 v.The impellers, shaft, and the housing/case of the pump should be stainless steel (AISI 304). The cable required to connect the pump to the RO board 3 lines 6mm (Control Panel) is included. with all requirements to complete the job, and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
4.16 | Control Panel Supply, Install, connect and operate Main Panel (MP) (180 H X100 WX60 D), double door, IP55, it contains bellow details: 1.PLC Control Type: Automatic, PLC Brand: Delta or equivalent, Power Supply: 24V Power supply 2.PLC Display: Touch Screen / DOP110IS, Power Supply: DRL-24V120W1EN 3.Soft starter (15 kw) includes (MCB 3 POLES, CONTACTOR, Over load, control accessories) 4.MCB Schneider, ABB or equivalent •125A x 1pc •60A x 1pc •32A x 2pcs •6A x 2pcs 5.Contractors 32D (Schneider, ABB or equivalent) x 5pcs 6.Over load x 3pcs All the necessary works required to put the control panel in place and duty is included. The cable should be running through conduit. All the works needed to complete the control panel of the RO is within the price. The work includes all requirements of operation to perform the job perfectly. | 1 | l.s | 0 | 0 | #DIV/0!
4.17 | Flow Meter Supply and install flow meter 20m3/hr, in-line type, PS material-made, sensitivity +-% 1.5. with all requirements to complete the job, and according to the supervisory committee instructions | 2 | pcs | 0 | 0 | #DIV/0!
4.18 | Low Pressure Gauge Supply and install pressure gage; range 1-10 bar. Liquid submerged; stainless steel material. with all requirements to complete the job, and according to the supervisory committee instructions | 2 | pcs | 0 | 0 | #DIV/0!
4.19 | High Pressure Gauge Supply and install pressure gage; range 1-25 bar. Liquid submerged; stainless steel material. with all requirements to complete the job, and according to the supervisory committee instructions | 3 | pcs | 0 | 0 | #DIV/0!
4.20 | Low Pressure Switch Supply and install pressure switch to regulate and monitor the pressure of the whole system. The pressure should be ranging (1-10) bar. with all requirements to complete the job, and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
4.21 | High Pressure Switch Supply and install pressure switch to regulate and monitor the pressure of the whole system. The pressure should be ranging (1-32) bar. with all requirements to complete the job, and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
4.22 | TDS meter Supply and install a TDS meter ranging (1-2000) ppm, in-line type. Best quality. with all requirements to complete the job, and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
4.23 | Voltage & Hz Meter Supply and install a voltage and Hertz meter. with all requirements to complete the job, and according to the supervisory committee instructions | 2 | pcs | 0 | 0 | #DIV/0!
4.24 | CIP system for the backwash (with Pump) Supply and install a CIP system for the back wash of the RO. The capacity of the system is 20 m3/hr. Pump hydraulic parameter (20 m3/hr, 4 bar), power: 4 KW, 5.5HP. The impeller, shaft, and the case should be stainless steel (AISI 304). The system includes tank PE 1,000 litter, 1", check valves, PVC pipe, pressure gauges, isolation valves, 3 phase motor. with all requirements to complete the job, and according to the supervisory committee instructions | 1 | l.s | 0 | 0 | #DIV/0!
4.25 | UV Sterilizer Supply and install UV sterilizer. The housing should be stainless steel (304) containing (4x55watt) lamp total power 220 watts, Voltage: AC 220V. Flow capacity 10 m3/hr. The UV sterilizer should be from high quality brand. with all requirements to complete the job, and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
4.26 | Ozone Generator Ozone Generator 3gm, O3 Output: 3 G/Hr, Power: 60W, Voltage: AC 220 – 240V/ 50-60Hz Concentration: 15-25 Mg/L, External Case: Stainless Steel 304, Working Condition: Up to 85% Humidity, -10~37 degree with all requirements to complete the job, and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
4.27 | Skid Supply and install heavy duty skid; stainless steel (AISI 304) to erect and mobilize the whole RO system on it in a robust way. with all requirements to complete the job, and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
4.28 | Water tank level sensor Supply, install, and commission electrical level sensor to indicate the minimum/maximum level of water in the tank so that the RO unit can turn on/off accordingly. All the wiring and accessories to complete the job are included and covered. with all requirements to complete the job, and according to the supervisory committee instructions | 2 | pcs | 0 | 0 | #DIV/0!
4.29 | Prefabricated Container Supply materials and manpower to install a prefabricated container and install the unit inside with the following specifications: Exterior Dimensions: Height 2.59m, Width: 2.44m Length: 6.06m Internal Dimensions: Height 2.38m, Width: 2.35m Length: 5.9m The container floor should be covered with aluminium chequer plate, installation of 2 tons AC unit and all of the required electrical power outlet and lights with all requirements to complete the job, and according to the supervisory committee instructions | 1 | l.s | 0 | 0 | #DIV/0!
4.30 | Miscellaneous - reserve for unforeseen additional small items required (such as screws and bolts, connectors, etc.) which are not included in the pre-items. | 1 | Lump Sum | 0 | 0 | #DIV/0!
4.31 | BRC Fence Supply materials, tools and manpower to install a new BRC mesh fence (Chain Link Mesh) of 3 mm thick, the size of opening not more than 6.5 cm and 1.8 m height around the RO system area to secure the management container other equipment, the fence shall contains three protection wires at the top of it and entance gate of 2 meter width, the work includes all installation and connection accessories, with all requirements to complete the job, and according to the supervisory committee instructions | 70 | m | 0 | 0 | #DIV/0!
4.32 | Metal Sunshade Works for Water Tanks supply materials, tools and manpower to install metal sunshade roof above the ground of 3m height, according to details below: Steel square column of 3x3 inch and 4 mm thick and the distance from column and another should not be more than 3 m Backfilling of sub-base layer of 20 CM and compacting it very well - Spreading Agricultural Nylon from the thick type on all the area under the shade - casting of 15cm floor with BRC layer - Base plate of 25x25 cm dimension10 mm thick to install the sunshade steel structure with concrete base floor using rot bolts of 18 mm diameter with all required works - Steel hollow square section for beams of roof structure of 3x3 inch dimensions and 4 mm thick. - Steel hollow rectangular section for sub beam 1.5x3 inch and 3 mm thick. - 0.6mm thick corrugated plates for the roof, fixed by screws and overlapped in order to prevent water leakage. The work includes all cutting and welding works, painting with anti-rust and three layers of oil paint for all steel structure with all requirements to complete the job, and according to the supervisory committee instructions. | 30 | m2 | 0 | 0 | #DIV/0!
4.00 | Sub Total RO System |  |  |  | 0 | #DIV/0!
5.00 | RO maintenance and consumable materials for 24 months
5.01 | 1. Cartridge (sediment) filters 1,200pcs. 2. Anti-Scalant materials: 6 drums, 20L each. 3. Chlorine liquid (CL2) materials with concentration 16%: 6 drums, 25 kg weight of each. 4. Anti-Chlorine Materials: 4 bags, each bag 25 kg weight. 5. RO membrane 10pcs | 1 | l.s | 0 | 0 | #DIV/0!
5.00 | Sub Total RO maintenance and consumable |  |  |  | 0 | #DIV/0!
6.00 | Electricl Connection, Lighting System and fire fighting
6.01 | Electrical twisted cable to connect Control Panel with the Main electrical system Supply, Install, test and commission twisted cable of (4x 25 mm2) to connect between Control Panel with the Main electrical system, with the aluminium conductor , the price should includes all the connection and installation accessories , manholes and its work, cable terminals, connectors according to the wire size needed, hocks , with all the required works to complete the job and according to the supervisory committee instructions | 50 | m | 0 | 0 | #DIV/0!
6.02 | Electrical Flex Cable to Feeding lights Supply, Install, test and commission flex cable of (2x1.5) mm² to connect between the lighting and the control panel, the price should include all the connection and installation accessories, circuit breaker, cable terminals and metal parallel groove connectors, according to the wire size needed , with all the required works to complete the job and according to the supervisory committee instructions | 50 | m | 0 | 0 | #DIV/0!
6.03 | lamp 100W Supply, install and connect 100 watt outdoor LED Street lamp(excellent type and economic); Aluminum, IP66, Waterproof, with all the required works to complete the job and according to the supervisory committee instructions | 4 | pcs | 0 | 0 | #DIV/0!
6.04 | AC / Split device 2 Ton Capacity Supply, Install, test and commission Split 2 tons units 24,000 BTU Single phase of heating and cooling invertor R410 Economic and environmental (TOSOT or equivelent) with good electrical protection device and with Circuit 30 amp MCB installed as per instruction of supervising Engineer. the price include wire connections using 3*4 mm2 and AC condensate dewatering: PVC or PPR pipes.with all the required works to complete the job and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
6.05 | Intental electrical connections Supply materials, tools and manpower to complete all electrical connections for the container, the work includes, fixing of three plugs and three switchs of 13 AMP and one switch of 45 AMP for the Split Unit, also two internal lights of 45 WAT, the price includes all required wires, connections, cable trays..etc with all the required works to complete the job and according to the supervisory committee instructions | 1 | l.s | 0 | 0 | #DIV/0!
6.06 | Powder type fire extinguisher Deliver and assemble, conceived and designed in accordance with EN 3. Pressure lever faucet (brass), 1-handle operation, internal CO2 pressure gas steel bottle. 9 ltr. or 12 ltr. content, freeze-proof to -30° C (AB), with spray nozzle. Ø 190 mm, height 550 mm. Performance classes / ratings 21 A and 183 B, extinguishing agent units (LE) 6 Permitting in accordance to the governmental rules and regulations. with all the required works to complete the job and according to the supervisory committee instructions | 2 | pcs | 0 | 0 | #DIV/0!
6.07 | CO2 type fire extinguisher Deliver and assemble, conceived and designed in accordance with EN 3. Pressure lever faucet (brass). 1-handle operation. Internal powder. Permitting in accordance to the governmental rules and regulations. with all the required works to complete the job and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
6.00 | Sub Total Electricl Connection, Lighting System and fire fighting |  |  |  | 0 | #DIV/0!
7.00 | Generator Works
7.01 | Concrete Floor Layer Supply, tools, materials and manpower to cast concrete floor 15 cm thickness with mixture 1:2:4 reinforced with steel reinforcment of 12mm two layers (10 cm c/c) over a layer of sub-base 15 cm and surrounded by soild concrete blocks. The price includes cement plastering for the walls (inside and outside) with all the required works to complete the job and according to the supervisory committee instructions | 20 | m2 | 0 | 0 | #DIV/0!
7.02 | Generator Shade Supply, tools, materials and manpower to install a generator shade 4*4 m and height 2.5 m (for the generator and the fuel tank) made of steel frame (5x5 cm, 2mm thickness) and coverded by of BRC 5x5cm, 5mm for the sides and by Kerby for the roof, the price includes installing a door (2x1 m) and a galvanized steel plate exhaust to be connected to the exhaust of the generator and painting of the frame with 2 layers of anti-rust paint and 1 layer of colored paint. with all the required works to complete the job and according to the supervisory committee instructions | 16 | m2 | 0 | 0 | #DIV/0!
7.03 | Generator Supplying, installing and operating a generator (30 KVA PRP, 400V, 3 PHASE, 50 HZ) sound insulated (canopied) and super silent. full automatic, motor quality (PERKNZ) (original type) turbocharged aspiration, water cooling system, Stamford Alternator, AVR excitation system provided with all protective devices and electrical gages with changeover switch including new electrical board. The price including supplying, installing and testing complete earth system with 3 copper rod (2m) for each and steel canopy (cover), with warranty 1 year or 1000 hours operating from the setting up and operating, the price includes fire extinguisher (CO2) type 10 kg weight according to the instructions of the site engineer. | 1 | pcs | 0 | 0 | #DIV/0!
7.04 | Fuel Tank supplying, installing and connecting, fuel metal tank, capacity 2000 liter of 4 supports, guage 16 with fuel filter and volume meter. The price includes connection between tanks and Generator with all fitting required with all the required works to complete the job and according to the supervisory committee instructions | 1 | pcs | 0 | 0 | #DIV/0!
7.00 | Sub Total Generator works |  |  |  | 0 | #DIV/0!
8.00 | Solar System Works
8.01 | Solar Panels and System Supply materials, tools, machinary, manpower, and expertise to install, test, and connect a complete PV solar system, with the following specifications: - 45 Solar Panel, with dimensions (L130 X W220 X Thickness 4cm) - total capacity: 24 kw - PV panels: 545 w half cut – mono Crystalline Module - Hybrid Solar Inverter: 8 kw x 3, "SUNNY TRIPOWER CORE1" or equivalent - Monitoring and control system: "SMA DATA MANAGER M" or equivqlent, compiled with the inverter, wifi connectivity. - all integrated system including DC distribution box, junction boxes, DC & AC cercuit breakers, boards, and all other requirements according to the instruction of the supervisor engineer. - Steel structure: must be of galvanized steel, mechanically connected, re-structurable, with aluminum caps. - all catalogues of devices must be submitted and approved by the supervisor engineer. | 1 | l.s | 0 | 0 | #DIV/0!
Solar batteries X 12 Pcs Supply materials and install Lithium-ion batteries, LiFeP04, 6000 cycles, 17.92 kWh, 48 V, nominal capacity 350 Ah, DoD not less than 80%. Each battery pack should contain an LED display, input and output connectors. Battery should be equipped with Charging Overvoltage Protection, Discharge Undervoltage Protection, Discharge Overcurrent Protection, Charging Overcurrent Protection, Short Circuit Protection, and Temperature Protection. Price includes supplying materials and connecting the batteries to the existing solar system using Photovoltaic Power cables (4 mm2, max. DC Voltage 1.8 kV, Halogen free, Flame Retardant, Low Smoke Emission), 500 mm busbars in sufficient lengths according to the instructions of the supervising engineer, cable trays according to the lengths and sizes specified by the supervising engineer, and all other requirements according to the instructions of the supervisor engineer.
Electrical board DC X 1 Pcs Supply materials and install 60*80 cm board for DC contains 3 DC circuit breakers 25 A, 5 AC circuit breakers 32 A, and 5 SPD's (Surge Protection Devices). The board should collect all the cables from the solar panels. All the SPD's should be connected to the earth system through a suitable size busbar.
Electrical board AC X 1 Pcs Supply materials and install 60*80 cm board for AC contains 160 A main circuit breaker X 2, 4 Poles, 3 Phase. The main circuit breaker should be connected to 4 suitable size busbars according to the instructions of the supervising engineer. The board should also contain 3 AC circuit breakers 32 A. The board should collect all the cables from the inverters.
Monitoring screen X 1 Pcs Supply materials and install 24 inches display with wifi connectivity to show the current status and power details. The display should be connected to the solar system and located a suitable location according to the instructions of the supervising engineer.
7.00 | Sub Total Solar System |  |  |  | 0 | #DIV/0!
Summary of Positions
1.00 | Mobilization and Demobilization |  |  |  | 0 | #DIV/0!
2.00 | Excavation and Backfilling |  |  |  | 0 | #DIV/0!
3.00 | Piping network |  |  |  | 0 | #DIV/0!
4.00 | RO System |  |  |  | 0 | #DIV/0!
5.00 | RO maintenance and consumable |  |  |  | 0 | #DIV/0!
6.00 | Electricl Connection, Lighting System and fire fighting |  |  |  | 0 | #DIV/0!
7.00 | Generator works |  |  |  | 0 | #DIV/0!
8.00 | Solar System |  |  |  | 0 | #DIV/0!
Total Sum over All |  |  |  |  | 0 | #DIV/0!