# Chlorine Generation Unit:

  - Specific chlorine production capacity (g/h or kg/h).

The required units: Two units for two different locations as follows:

  - Sulaymaniyah- Halabja- Khurmal Water Project (100 Cubic meters per hr.).

The required capacity of the Chlorine generation unit for this project is 220 g/hr.

  - Erbil- Koya- Taqtaq Water Project (200 Cubic meters per hr.).

The required capacity of the Chlorine generation unit for this project is 450 g/hr.

  - Method of chlorine production (e.g., Electrolytic conversion of salt “Salt Chlorine Generator”).

Required salt consumption range: 4.0 to 6.0 kg of Salt per kg of produced chlorine.

The temperature range, coldest and hottest, vary between -5 to +50 Celsius degree across the seasons. Consider heater and/or Cooler if the chlorination unit does not function in the mentioned range of temperature.

# Brine Tank:

- Material of construction: HDPE or PPR

- Capacity: According to the generation unit capacity. Minimum capacity should match the generation unit productivity.

- Manual and automatic salt filling.

It includes all the required accessories for the installation and connection of the tank to the system.

# Safety Warning System:

- Hydrogen gas detection system.

- Alarms for low voltage, high voltage, overtemperature, water flow error, and other critical parameters.

- Emergency shutdown functionality.

# Control and Monitoring System:

- User-friendly interface for monitoring and controlling the chlorine production process.

- Remote monitoring and control capabilities.

- Integration with existing systems and controls.

# Maintenance Kit: Four kits, two for each unit.

- Tools and equipment for regular maintenance.

- Maintenance schedule and guidelines provided by the manufacturer.

Chemical Storage:

- Appropriate storage tanks for sodium hypochlorite solution

- Dosing pumps for the controlled release of produced chlorine.

The required size for the storage tank and the dosing pump must be compatible/match with the Chlorine generation units.

Installation and Operation:

- The awarded company is responsible for installing the whole system and the provision of the necessary materials, fittings, pipes, valves, parts, etc. for the installation purpose of the units.

- Training for at least three operators and maintenance personnel.

- Comprehensive operation manual.

# Certifications and Compliance:

- The origin country of the units should be western European.

- Ensure the unit meets the relevant industry standards and certifications and the origin certificate and catalogues should be submitted.

- Compliance with environmental and safety regulations.

# Additional Accessories:

- Test kits for chlorine concentration and other relevant parameters.

- Acid cleaning system for the electrolysis cell.

- Ventilation and hydrogen dilution system

- Flow meter and Level sensor.

- Any other accessories that essential for the installation, the company should suggest to add with the price breakdowns.