## TECHNICAL SPECIFICATIONS
SUPPLY OF SCADA SYSTEM IN PUMPING STATION
| TECHNICAL SPECIFICATIONS | COMPARATIVE SPECIFICATION / REMARKS
A - Minimum technical requirements. |  | Comparative specification / remarks should indicate any deviation from technical parameter or functional description of tender specification or confirmation with "Yes" and if applicable further particularities.
SUPPLYING, HANDLING , DELIVERING AND INSTALLING SCADA system at Water pumping station
1 | SCADA and PLC
1.0 | ISCADA (Supervisory Control and Data Acquisition) software The system software includes installation, programming, testing, and operating PLC and SCADA. Also, included the screen and HMI graphics for the monitoring system. The overall design (ex. input and output data) for commissioning the package is included. Clearly state the project's objectives, including: Control and automation of 7 booster pumps. Monitoring of 2 flowmeters. Measurement of water level. Monitoring of water quality (PH, chlorine ratio, turbidity). Supervision of 7 pressure gauges on the pipeline. SCADA Software: supports hardware components and provides the necessary features for data acquisition, control, and monitoring. The type of SCADA software should be Wonderware, Ignition, Siemens WinCC, and Inductive Automation's Ignition or any other equivalent type. The work includes SCADA local Server and Workstation: Set up a dedicated server or workstation to run the SCADA software. Ensure that these computers meet the software's system requirements. Other software requirements: data logging, alarming system, trending visualization, system security, remote access, reporting, and Ensuring that all sensors and devices support industry-standard communication protocols such as Modbus, OPC, or Ethernet/IP for seamless integration with the SCADA system. Training operators for how-to-use the system is included to the work.
1.1 | PLC (Programmable Logic Controller) requirements (hardware) for 7 pumps PLC/EMI panel Software / Hardware for Monitoring / Controlling the pumps running including Control Cabling, UPS, Electrical Wiring, Ethernet with Switch, database, Electrical/PLC panels, Electrical Actuators for the 7 Valves DN 800 (with supply MCC panel for valves), pressure switches for pumps and GPRS Modem-based wireless communication modem for RTU/PLC capable to gather and transmit data from remote the site to control station. Online UPS with battery bank ( 3kva, 1 hour backup) . Redundancy: Consider redundancy for critical components like servers and network connections to ensure system reliability. The work includes transferring pump thermal sensor data to the SCADA system.
2.0 | Monitoring tools/devices to be linking with the SCADA
2.1 | Flow meter 2 Ultrasonic Water Meters for dia 800 mm: flowmeter with appropriate communication interfaces (e.g., Modbus, Ethernet/IP) to measure and transmit flow data.
2.2 | Level sensors one Water Level Sensor: A water level sensor to measure the water level in the station's tank or reservoir.
2.3 | Water quality analyser Water Quality device with Sensors from the 2 outlet pipes: pH sensor, chlorine ratio sensor, and turbidity sensor with compatible communication interfaces. pH Analyzer 0-14 pH Single Channel Turbidity Analyzer, NTU Range : 0-500 NTU ; 100 to 230 VAC Free Residual Chlorine, mg/l Range: 0-5ppm; 100 to 240 VAC
2.4 | Pressure Gauges 7 Pressure Gauges: pressure transducers or gauges to monitor pressure at different points in the pipeline. Including pressure switches.
Note related to the above requirments Shall be manufactured by ABB, Endress+Hauser, Siemens or equivalent to be adequate with the SCADA system. The work includes control cabling, wiring, switches and sensors, all to be linked with the PLC panel. Other electrical requirements for 7 pumps (panel, thermal protection magnetic protectors, conductors, circuit breakers ,voltage protectors, and relays) all the systems to be connected with the existing VFD/type ABB
B. DELIVERY
1 | The delivery and installation to the selected location is Iraq (Diwaniyah Gov.), and the delivery and installation will be under the responsibility of supplier coordinated with GIZ.
2 | transportation, installation, will be under the responsibility of the supplier and included in the financial offer.
C. REMARKS AND CONDITIONS
1 | Close coordination with Directorates of water during installation of SCADA system, electrical parts and flow meters.
2 | Provide a certificate of origin from the production company for essential parts of the system.
3 | Product specifications, criteria table must be attached with tender package, and Technical Data sheets, ISO and certificate of origin of all products must be provided. Warranty (after sell maintenance) (min.1year) confirmation must be provided. As well, Installation manuals must be provided. Describe the support and maintenance services you will provide after the system is installed and commissioned.
4 | Selecting a SCADA software, it's essential to consider the following: Compatibility with your existing hardware and communication protocols. Scalability to accommodate future expansions or changes. Ease of use for your operators and engineers. Support and training options provided by the software vendor. Budget constraints and licensing costs.
5 | Bidder must submit the technical proposal for installation, working schedule plan of implementation including technical-related procedures with sketches for installing the whole system
6 | The bidder will be responsible for all custom fees, clearance and taxes at borders and any other transportations that need governmental fees if required.
7 | The Bidder must provide the following below documents with the bid documents, in order to substantiate their eligibility for the contract being awarded:
8 | Technical and professional capacity:
9 | In the last three years prior to this bid, the company has gained experience [SCADA services in Water network, metering, treatment units & water spare parts supply] and can substantiate this with at least three reference projects (includes the client's emails, contact numbers, contract value).
10 | Provide 3 references for similar services in Iraq that have been provided to reputable clients in the past 5 years and previous relevant experiences (Semester from 2018-2023)