## Cold Room
Annex -A- Cold Room Technical specifiactions
General Notes: 1. The cost for all the items listed below includes the provision of materials, equipment, transportation, installation, and any other necessary accessories and work. Any relocation or modification of existing items or services will be directed by DRC Team. 2. Samples of the items and materials to be used in this project must be provided to DRC team to be approved. 3. For the regrigeration unit main parts ( Compressor, Condenser, Evaporator) a Warranty and certificate of origin must be provided, and a data sheet that contains the technical specifications for the provided items must be provided if possible. 4. The temperature setting for the cold room shall be 2-5 C Degree (it will be used for storing dairy)
# | ITEMS DESCRIPTION | UNIT | Req. QTY | Offered unit price (IQD) | Offered Total Price (IQD) | SAMPLE (PICTURE)
1 | Structure: Supply and install sandwich panels for the cold room ( Roof, Walls and ground) including all required insallation materials and according to the below specifications: - Materials: Galvanized, pre-fabricated, painted in white color - Insulations: Polyurethane foam , fire resistant. - Thickness: 10 cm, a blind rivets to be used in the insallation process with appropriate size. - The ground to be falt with zero slope. - Closing any gaps or openings. - All inner corners must be covered in aluminum angle plate - Preferred to be Turkish-made. - The room must be installed with all the above mentioned material, and any needed accessories or parts to work correctly as a cold room. - The work must be according and approved by DRC team. - Samples required (photos showing the requsted thickness) | M² | 72
2 | Door: Supply and install insulated hinged door used for cold rooms with the below specifications: -The door closely connected with the overall cold room, and the hinged door is pre-installed, which is integrated with the cold storage to ensure the tightness. - Type: Fully buried hinged door -Material : sandwitch panles and Aluminum -Insulations: Polyurethane foam , fire resistant. -Dimensions of 2 m * 1 m. - Door thickness: 10 cm - Frame : Aluminum , 10 cm wide with appropriate thickness not less than 3mm. -Handle and locks to be made specillay for cold room - Thermostat clock preferred to be Italy-made. - Painted with special Hygienic paint (Antibacterial paint) food safe. - Accessories: three hinges, stop door, handles and locks. - All accessories and any other parts that it is needed must be provided for proper installation. - All the openings or gaps must be closed - Provide a PVC strip curtain "transparent" with fixing strip to put in the inner side of the room. - The work must be according and approved by DRC team. - Samples required (photo showing the requsted thickness, accessories that will be used, thermostat and PVC strip curtain) | No. | 1
3 | Lights and switch: Supply and install led lights and switch with cover, with the below specification: - Fully sealed design, Imported silicone seal and Low temperature resistance. - Type: 60 watt, white color,IP65. - Product size:165*84*70 mm - Switch rated current: 13 Amp - lights Similar to the attached photo. - The work includes all accessories and wiring to work correctly. - The work must be according and approved by DRC team. - Samples required. | No. | 4 |  |  | #VALUE!
4 | Shelving: Supply and install strong standard shelving rack with the below specification: - Material: stainless Steel for structure and shelf panels - Material grade: 304 stainless steel - Stainless steel corner connectors - Measurement: 4m x 0.5m x 1.8 m (LWH), the clear distance between the two shelf panels is 75 cm. The total length could be divided into two. - Structure: the distance from the ground at least 10 cm ,thickness = min 4 mm, the frame must contain diagonal and horizontal strut thickness= min 3 mm , cross bracing to be used in the back with minimum thickness= 3 mm, add one horizantal bracing every 1 meter for extra support .Install a central horizontal brace under each level, vertical support posts to be used. - Racks " shelf panels": perforated steel surface - Rust guaranteed - Max load capacity for each shelf panel: 600 kg - The work must includes all the parts that will be needed for perfect installation and loading capacity. - The work must be according and approved by DRC team. - Samples required(showing thickness required and a prove showing the material grade) | No. | 3
5 | Stainless Steel Checker Plate: Supply and install checker plate for the ground of the cold room for extra protection with the below specification: - Material: Stainless steel - The pattern for the face of the plate to be round bean-shaped, dot-shaped, oblate mixed shape. - Plate Thickness: 3 mm -The work must be according and approved by DRC team. - Samples required (showing thickness) | M² | 15.75 |  |  | #VALUE!
6 | Refigerant Unit (Cooling Unit): Supply and install a cooling unit with the below specifications: Compressor: R404A refrigerant similar to a Bitzer compressor - 5 HP -Current Rating: 15-20 A Max - Compressor type: Semi-hermetic screw compressor -Voltage: 380-400V, 3~50 Hz -Maximum Ambient Temperature (TS Max): 50.0°C -Minimum Ambient Temperature (TS Min): -35.0°C Features: Reliable performance and efficiency -Ensure that the unit is installed according to manufacturer guidelines and is suited to the specific cooling requirements of the cold room. -Condenser Dimensions: min length =1380 mm, width= 230 mm - 5 HP , Condenser preferred to be Turkish made. - Evaporator fan: 2 Fan, 500 mm, speed 1330 rmp , Current 6.2A,Voltage 230 , 50 Hz - Casing type: ESB painted galvanized steel -Fin material: Aluminum **Internal Unit Specifications: - Dimenstions: approximately 140 cm in length, width 54 cm Power Supply: 230V, Single Phase, 50 Hz , 5 HP Defrost Voltage: 220V Refrigerant: HFC/HCFC Fan Current: 1.46 A, 2 fan 400 mm in diameter Test Pressure: 34 bar / max. operating pressure : 22 bar - the work includes the special defrost specifications ( Heaters). - for the accessories that it needed in the installation preferred to be simliar to Danfoss brand -The work must be according and approved by DRC team. -Samples required. -Warranty: Provide a warranty for the unit, detailing coverage and duration | ACCY | 1
7 | Electrical control panel: Supply and install an electrical panel with the below specifications: -Brand: Similar to Schneider -Features:High-quality components and construction -Designed for reliable performance and safety - Steel electrical distribution metal Box - Main circuit breaker 3-phase , 63Amp -Light signals No.= 3 -Gauge for Current, Voltage and frequncy - One circuit breaker switch single pole 10 A - Digital protection device - Phase failure - mulity stage timer - Relay: No.=2 , 10 Amp - 3 phase Contactor with over-load ,25 A No.=2 - Contactor over-load - Digital adjustable thermostat - Emergency stop button - wiring and connectors and plastic tray cable - The work includes all the assessories, parts and wiring that it's needed for fully and correct installation for the cooling unit. - The work must be according to/approved by DRC team. - Samples required (photos for the parts with detailed specification) -Provide a certificate of origin. | ACCY | 1 |  |  | #VALUE!
8 | Electric cables: Supply and istall an electrical cables with the below specifications: - Size: 2x2.5mm - Type: PVC insulated- twin flat cable. - Conductor type: Solid. - Conductor Material: Copper. - Permissible operating tem.: -5 C - 70 C - Test voltage (AC): 2KV. The cost includes Provision and installation of PVC cable tray -The work must be according and approved by DRC team. - Samples required (photo) | M.L | 20
9 | Iron Shed "Corrugated Sheets": Supply and install iron shed with the below specifications: -Dimensions: 4.5m x 5.5 m - Type: roof - Materials: Galvanized, corrugated sheets - Thickness: 0.8mm - Structure: Using rectangular hollow iron tube 5 x 5 cm, plate thickness 2mm, as frame and as Vertically support every 1.5 m C/C, distance between Self-drilling screw 30 cm. - The structure must be painted by one layer of anti-rust paint and two layer of oil paint. -The work must be according and approved by DRC team. - Samples required (photo showing requsted thickness for the sheet and structure) | ACCY | 1
10 | PVC insulated round cable: Supply and install electrical power cable with the below specifications: - Size: 4x6mm - Type: PVC insulated- twin round cable. - Conductor type: Solid. - Conductor Material: Copper. - Permissible operating tem.: -5 C - 70 C - Test voltage (AC): 2KV. The cost includes Provision and installation of PVC cable tray if possible. - The work must be according and approved by DRC team. | M.L | 25
| Total price (IQD) |  |  |  | 0