GTP Compliance Sheet

The following technical data shall be furnished and filled by the bidders:

Electrical Item / PV Monocrystalline Solar Panels:

| No. | Description | KOHRW Requested specifications | Bidders Offered specification |
| --- | --- | --- | --- |
| 1 | Electrical specs |  |  |
| 1.1 | Model: | BIFACIAL MODULE |  |
| 1.2 | Name of manufacturer | Longi, Jinko Q-Cell, Bluesun, LG, Gamko, or equivalent |  |
| 1.3 | Country of Origin |  |  |
| 1.4 | Type of Module | Monocrystalline / Half-cut/ Class A |  |
| 1.5 | Max. power output | Min 620W |  |
| 1.6 | Front Cover | The facing glass must be Tempered, PV grade with Low iron and high transmission, Thickness shall be min 3.2 mm, Anti-Reflection Coating, Tempered Glass, The transmission shall be > 93 %, Textured to trap more light. |  |
| 1.7 | Frame | Anodized Aluminium Alloy with mounting and drainage holes. |  |
| 1.8 | Module efficiency | ≥ % 23.0 |  |
| 1.9 | Voltage at max power | 40– 46 V |  |
| 1.10 | Current at max power | 10 - 14 A |  |
| 1.11 | Open circuit voltage | 49 – 50 V |  |
| 1.12 | Short circuit current | 11 – 14.5A |  |
| 1.13 | System Voltage | Not less than 1500 VDC |  |
| 1.14 | Certification and regulatory standards | CE, IEC 61215/ 61730/ 61701/62716, TUV, ISO 9001/ISO 14001, UL certificates or equivalent standards. |  |
| 1.15 | Max series fuse rating | 30A |  |
| 2 | Mechanical specs |  |  |
| 2.1 | Module Dimension | To be filled |  |
| 2.2 | Cells | To be filled |  |
| 2.3 | Weight (kg) | To be filled |  |
| 2.4 | anti-reflective coating type | Anti-reflection glass |  |
| 2.5 | Junction box IP rating | IP68 |  |
| 2.6 | Connector type | MC4 or MC4 compatible |  |
| 2.7 | Fire performance | Type II (in accordance with UL1703)/Class C(IEC61730) |  |
| 3 | Working Conditions & Temperature |  |  |
| 3.2 | Temperature coefficient (Pmax) | -0.30%/℃ |  |
| 3.3 | Temperature coefficient (Isc ) | +0.046%/℃ |  |
| 3.4 | Temperature coefficient (Voc ) | -0.25%/℃ |  |
| 3.5 | Operation Temperature | -40 to +85 ℃ |  |
| 4 | Warranty | Power output warranty: not less than 12 years over 87.4%, 30 years over 60%. |  |
| 5 | Submit Manufacturer certification and test reports |  |  |
| 6 | Submit Detail drawing brochure catalogue. |  |  |

Electrical Item / SOLAR hybrid Inverter (High voltage)	:

| No. | Description | KOHRW Requested specifications | Bidders Offered specification |
| --- | --- | --- | --- |
|  | Electrical Specification |  |  |
| 1 | Make/Brand/Model: |  |  |
| 2 | Name of manufacturer | Fronius, Must, Deye, ABB, Gefran, Solis, Sofar, or equivalent |  |
| 3 | Country of Origin | Europe, USA, Japan, Or Equivalent |  |
| 4 | Nominal Power | 50 kW (high voltage) |  |
| 5 | AC voltage / Frequency (input & output) | 3/N/PE, 220 V / 380 V, 230 V / 400 V/ 50 Hz |  |
| 6 | Nominal output current | 60 A / 57 A |  |
| 7 | Maximum input current | 76 A / 72 A |  |
| 8 | Feed in to grid | Programable |  |
| 9 | Energy consumption priorities | Programable |  |
| 10 | Output Wave Form | Pure Sine Wave |  |
| 11 | Protection category | IP 66 |  |
| 12 | Solar installation: |  |  |
| 13 | Maximum input power | Up tp 100 kW |  |
| 14 | MPPT voltage range (Vmpp) | 150 V- 850V |  |
| 15 | Maximum input current (Impp) | 4 × 40 A |  |
| 16 | Maximum short-circuit current (Isc) | 4 × 60 A |  |
| 17 | Maximum input voltage (Voc) | 1000 V |  |
| 18 | Maximum efficiency | DC to AC: > 97.8 % |  |
| 19 | NO. of MPP Trackers | 4 |  |
| 20 | Strings per MPP Tracker | 8 |  |
| 21 | Battery & Charger: |  |  |
| 22 | DC range voltage | 150-800 Vdc |  |
| 23 | Maximum discharge current | 70 A × 2 |  |
| 24 | Maximum charging current | 70 A × 2 |  |
| 25 | Type of batteries | Lithium |  |
| 26 | Efficiency | 98.5% |  |
| 27 | Battery charge | Programable |  |
| 28 | Battery discharge | Programable |  |
| 29 | INTERFACE: |  |  |
| 30 | Parallel Function | 140 A |  |
| 31 | Communication | CAN / RS485 |  |
| 32 | ENVIRONMENT: |  |  |
| 33 | Relative Humidity | 0% ~ 95% |  |
| 34 | Operating Temperature | -25 ~ +60°C |  |
| 35 | Cooling concept | Intelligent fan-cooling |  |
| 36 | Altitude | 4000 m |  |
| 37 | Standards | G99, VDE-AR-N 4105/VDE V 0124, EN 50549-1/EN 50549-10, VDE 0126/UTE C 15/VFR:2019, NTS 631/RD 1699/RD 244/UNE 206006/UNE 206007-1, CEI 0-21, C10/11, NRS 097-2-1, TOR, EIFS 2018.2, IEC 62116, IEC 61727, IEC 60068, IEC 61683, EN 50530, MEA, PEA,PORTARIA Nº 140, DE 21 DE MARÇO DE 2022, IEC/EN 62109-1/-2, IEC/EN 61000-6-2/-4, EN 55011 |  |
| 38 | Dimension | To be filled |  |
| 39 | Weight | To be filled |  |
| 40 | Warranty | Min. 5 years |  |
| 41 | Submit Manufacturer certification and test reports |  |  |
| 42 | Submit Detail drawing brochure catalogue. |  |  |

Electrical Item / Battery Bank:

| No. | Description | KOHRW Requested specifications | Bidders Offered specification |
| --- | --- | --- | --- |
| 1 | Make/Brand/Model: | To be filled |  |
| 2 | Name of manufacturer | To be filled |  |
| 3 | Country of Origin | To be filled |  |
| 4 | Type | Lithium Ion battery |  |
| 5 | Voltage | 307.2V |  |
| 6 | Capacity | 100Ah |  |
| 7 | Nominal Energy(kWh） | 30,7 kwh |  |
| 8 | Dimensions (Lx W X H) | To be filled |  |
| 9 | Weight | To be filled |  |
| 10 | Life times (25 ℃) | 15 Years |  |
| 11 | Life cycles ( 80%DOD, 25 ℃) | 6000 Cycles |  |
| 12 | Storage time / temperature | 5 months @25 ℃, 3 months @35 ℃, 1 month @45 ℃, |  |
| 13 | Operation temperature | -20 ℃ to 60 ℃ <95%R.H Relative Humidity. |  |
| 14 | Lithium Battery Standard | IEC62619-22, IEC 61427, UL1973, UN38.3 , ROHS, CE-EMC |  |
| 15 | Enclosure protection rating | IP20 |  |
| 16 | Operating voltage | 614.4 Vdc |  |
| 17 | Max charging voltage | 700.8Vdc |  |
| 18 | Max charging current | 100A |  |
| 19 | Max discharging current | 100A |  |
| 20 | Submit Manufacturer certification and test reports. |  |  |
| 21 | Submit Detail drawing brochure catalogue. |  |  |